ANNEXURE B:	FUNCTIONAL AND TECHNICAL SPECIFICATIONS FOR INTEGRATED SECURITY SYSTEMS

SEPTEMBER 2022

The information contained within this document is confidential to ATNS in all respects and it is hereby acknowledged that the information as provided shall only be used for the preparation of a response to this document.  The information furnished will not be used for any other purpose than stated and that the information will not directly or indirectly, by agent, employee or representative, be disclosed either in whole or in part, to any other third party without the express written consent by the Company or its representative.

Table of contents

1	FUNCTIONAL SPECIFICATIONS FOR INTEGRATED SECURITY SYSTEMS	10

1.1	SECURITY MANAGEMENT SYSTEM (SMS)	11

1.1.1	General Description and System Overview	11

1.1.2	Security Sub-System Integration	11

1.1.3	Security Management functions	12

1.1.4	Security Large Area Network	12

1.1.5	Integration Description	13

1.1.6	System Configuration	18

1.1.7	System Performance	19

1.1.8	Minimum Hardware Requirements	20

1.1.9	Minimum Software Requirements	20

1.1.10	Operator Visual Display Units	21

1.1.11	Software	22

1.1.12	Archiving Historical Data	24

1.1.13	System Status	27

1.1.14	Current Alarm Window	28

1.1.15	Graphical Display	29

1.1.16	Security Management Functions	30

1.1.17	Visitor Management Module	40

1.1.18	Maintenance and Spare equipment	43

1.1.19	Graphical User Interface	43

1.1.20	OPERATIONS AND INCIDENT MANAGEMENT SYSTEM	45

1.2	ACCESS CONTROL SYSTEM	54

1.3	INTRUDER ALARM DETECTION SYSTEM	81

1.4	CCTV SYSTEM	84

1.5	NETWORK BACKBONE SYSTEM	127

1.6	PERIMETER INTRUSION DETECTION SYSTEM	131

1.7	RAISED ACCESS FLOOR SYSTEM	141

1.10	INTERCOM SYSTEM	158

1.11	SECURITY FENCE PERIMETER LIGHTING	160

1.12	EARTHING SYSTEM	160

1.13	TRANSIENT VOLTAGE SURGE SUPPRESSION	163

1.14	REMOTE / OFFSITE MONITORING	164

2	TECHNICAL SPECIFICATIONS FOR INTEGRATED SECURITY SYSTEMS	165

2.1	ACCESS CONTROL SYSTEM	166

2.2	ALARM SYSTEM	175

2.3	CCTV SYSTEM	180

2.4	SYSTEMS CONTROL	190

2.5	NETWORK BACKBONE SYSTEM	193

2.9	INTERCOM SYSTEM	216

2.10	PERIMETER INTRUSION DETECTION SYSTEM	219

2.11	SURGE PROTECTION DEVICES (SPDs)	221

2.12	CABLING)	222

2.13	POWER SUPLIES (Industrial DIN Rail Mounted Power Supplies)	223

2.14	HIGH SECURITY FENCE SYSTEM	224

2.15	PERIMETER LIGHTING SYSTEM	228

2.16	RETAINING WALL	228

2.17	Accessories	228

2.18	Markers and Nameplates	228

# FUNCTIONAL SPECIFICATIONS FOR INTEGRATED SECURITY SYSTEMS

## SECURITY MANAGEMENT SYSTEM (SMS)

### General Description and System Overview

The Contractor shall supply, install and commission a fully integrated multi-workstation security management system to facilitate the control and monitoring of all security sub-system components by means of a mouse activated operator workstation.

Operator Workstations shall be located within each local control room within the site as well as the Central control rooms offsite.

The Contractor shall provide all materials, labour and supervision required to install, commission and document the complete system as required by this specification, and as indicated on the accompanying drawings.

The SMS offered shall have demonstrated proven operation in a minimum of five (5) facilities, and a list of reference sites shall be provided as part of the tender response.

### Security Sub-System Integration

The Security Management System (SMS) shall provide the integration platform for all Security Sub-Systems. It is a specific requirement of this tender that the SMS shall interface directly with all sub-system hardware by means of existing drivers supplied as part of the SMS software. Hardwired interface of one sub-system to another to achieve integration with the SMS shall not be accepted.

The SMS software shall perform all interlocking functions between the various subsystems i.e. the automated switching of CCTV images upon intercom selection, door alarms, fire alarms, intrusion detection etc. The SMS software shall be capable of configuring the necessary interlock functions either by providing a configuration table or an internal scripting site or a combination of the two. The programming of interlock functions within sub-system hardware/software as a means of achieving the required functionality shall not be accepted. The tenderer shall provide a description of the interface protocol for each sub-system hardware platform offered as part of this tender, in the clause by clause compliance statement to be returned with their submission.

The SMS software shall provide the necessary soft control functions to eliminate the need for any additional control components such as keyboards, joysticks or proprietary operator panels.

System operators shall be capable of controlling all functions of the sub-system hardware components via a single mouse driven operator workstation running on a Windows 10 or later operating platform within a single Security Management Application.

The following sub-system hardware components shall be directly integrated with the Security Management System by means of a high-level interface:

- Access Control based door locking system

- IP Intercom system

- IP based CCTV system

- Perimeter Intrusion Detection system

- Spikes & Boom Barrier system

- Motorized gates system

- Intruder alarm system

- Uninterruptible Power Supplies

- Backup Generator

The following devices shall be interfaced to the Security Management System via the PLC based door locking system by providing remote multi-I/O modules where required:

- Non-controlled door position switches (DPS)

- Over voltage suppression devices

- Standby Generator Sets

### Security Management functions

The Security Management System (SMS) shall provide the following software functions:

- Graphical representation of the sites by means of multiple area maps

- Control and Monitoring of PLC controlled Doors

- Control and Monitoring of Access Controlled Doors

- Control and Monitoring of Intercom Stations

- Manual and event-based selection of IP based fixed and PTZ CCTV cameras

- Control of Pan, Tilt, Zoom functions of CCTV Cameras

- Event based Black Screen Management of CCTV Cameras

- Configuration of Network Video Recording

- Event based retrieval of recorded video footage

- Control and Monitoring of Perimeter Detection devices

- Control and Monitoring of motorized gates

- Monitoring of centralized UPSs

- Monitoring of Duress Buttons

- Monitoring of Standby Generator sets

- Staff and Visitor Enrollment

- Spikes & boom barriers

### Security Large Area Network

A high speed 1GB high speed Ethernet network shall be supplied, installed and commissioned by the contractor, which shall provide system networking for all security sub-system hardware.

It is a specific requirement that all sub-system hardware shall interface either directly or by means of IP converters within the local equipment room in each building. All communications between buildings shall be IP based.

The LAN shall be installed in a star topology with the star point being situated at the most centrally located Security Equipment room in the site. Each local equipment room shall be equipped with a sufficient number of 24 port 10/100 Layer 3 Managed PoE Ethernet switches with a minimum of two 1GB uplink ports. Sufficient Switches shall be provided to enable the termination of all 10/100 devices provided.

The 1 GB Uplink ports shall be networked via fiber optic converters to the Central equipment room and terminated into a 24 port 10/100/1000 Layer 2 Switch.

The contractor shall supply and install all cables, enclosures, switches and any other components to make the system complete.

### Integration Description

#### PLC Based Door Locking Sub-System

The locking sub-system hardware shall be integrated with the SMS via a high-level Interface (HLI). The full functionality of the locking sub-system hardware shall be integrated with the SMS to provide enhanced features including but not limited to:

- Door Lock

- Door Unlock

- Door Inhibit

- Door Status monitoring

- Door Alarm annunciation

- Door auto-close

- Hardware fault diagnostics.

The locking sub-system shall control and monitor all electrically controlled swing doors, sliding doors and gates within the site.

The locking system control hardware (I/O points) shall be an integrated function of the door control module as described in this specification.

#### I/O Alarm Monitoring Sub-System

An Alarm monitoring sub-system shall be provided to monitor specific hardwired alarm I/O points within the site, which shall be managed by the PLC based door locking system hardware. Such Alarms shall include but not be limited to the following:

DPS monitored door alarms.

Standby generator alarms.

Surge Voltage alarms.

The alarm monitoring system control hardware (I/O points) shall be an integrated function of the door control module as well as the multiple I/O control modules described in this specification.

#### Access Control Sub-System

The Access Control requirement shall consist of two sub-components:

- Biometric Logon of Operator Workstations

Each Security Management System Operator Workstation shall be provided with a vandal resistant fingerprint reader for logging on to the Workstation. Operator’s commands and events shall be logged into the centralised database against the relevant Operators details.

- Biometric Access Controlled Doors

Each Access Controlled door shall be equipped with a Fingerprint Reader as detailed in the specification.

The following functionality shall be provided by the Access Control System:

- Staff Time and Attendance Management

- Visitor Management

#### Intercom Sub-System

The IP Intercom sub-system hardware shall be integrated with the SMS via a high-level Interface (HLI). The full functionality of the system shall be integrated with the SMS to provide enhanced features including but not limited to:

- Station Call-In

- Station Fault Analysis

- Call In Divert

- Call Answer

- Call Cancel

- Call-In Queuing

- Tamper Alarm monitoring

- Threshold Monitoring (Disturbance detection)

- Individual station Speaker and Microphone sensitivity adjustment

The Intercom system shall enable the selection of any individual or group of intercom stations by any operator workstation within the site.

#### IP Based CCTV Sub-System

A fully IP based CCTV System shall be integrated with the SMS via a high-level Interface (HLI) at each workstation or server. The full functionality of the system shall be integrated with the SMS to provide enhanced features including but not limited to:

- Camera to Monitor commands

- Sequence to Monitor commands

- Sequence programming commands

- Pan, Tilt, Zoom commands

- PTZ preset select commands

- PTZ preset save commands

- Monitor Blanking commands

- Black screen technology

Camera Types that are not available as direct IP cameras shall be converted to IP via a single channel H264 IP Video Encoder mounted directly at the camera position.

##### IP Based Network Video Recording Sub-System

A fully IP based Video Recording System shall be integrated with the SMS whereby all images are stored on Digital Video Recording Servers installed within the various security equipment rooms in the site. NVR’s shall be connected directly to the appropriate 24 Port managed switches within the local equipment cabinets.

The managed Ethernet switches shall be configured to limit the Video traffic onto the incoming 1Gb uplink ports on the switches, by restricting outgoing streams to those required for live video feeds based on Operator selection, and recorded video footage being reviewed by Central Operator Workstations or the Operations room.

In order to minimize traffic on the 1 GB uplink ports, the allocated recording stream on each of the Direct IP cameras or IP Video Servers shall be assigned to the IP address of the Network Video Recorders within the local subnet.

The full functionality of the NVR system shall be integrated with the SMS to provide enhanced features including but not limited to:

- Individual Channel Record and Stop commands based on other sub-system conditions such as Intercom, CCTV and Locking.

- Channel Playback select

- Play

- Stop

- Pause

- Back

- Left Jump

- Right Jump

- Left Shift

- Right Shift

- Plus

- Minus

- Log

- Search

The search and playback site shall be an integrated function of the SMS, and shall not require any third-party software platform to perform these functions.

Upon operator request the SMS system shall be capable of instructing the NVR system to playback video images to allow proper investigation of the visual event. The SMS management workstation shall be capable of recalling associated historical Video and Audio data based upon events logged to the event recording database on the severs.

System supervisors with the correct user level shall be able to query the event database as described in this specification and by double-clicking on a specific event shall be presented with the associated Video and Audio footage automatically.

#### Perimeter Intrusion Detection Sub-System

The Perimeter Intrusion Detection system shall be fully integrated with the Security Management System by means of a TCP/IP socket interface (High Level Interface), in order to carry out logical connections with other security sub-systems such as the CCTV and Digital Video recording systems.

The operator shall be able to select a graphical layout of the entire site, which shall also be automatically activated upon an alarm event from the perimeter fence system.

The Security management system shall be capable of, but not limited to the following monitoring and control functions relating to Perimeter Detection:

- Non-Lethal shock energizer loop open circuit status

- Non-Lethal shock energizer loop short circuit status

- Non-Lethal shock energizer loop normal status

- Digital expansion Input status

- Field Node communication status

- Field cabinet tamper status

- Field Node logic monitoring status (Light on status)

- Field Node battery charger voltage

- Sensor alarm Acknowledge

- Loop alarm Acknowledge

- Sensor alarm Reset

- Loop alarm Reset

- Inhibit Digital Expansion Input alarm

- Inhibit Field kiosk Tamper alarm

- Individual Sensor sensitivity setting

- Loop sensitivity setting

#### Centralized UPS System

The Dual redundant centralized UPS's shall be fully integrated with the Security Management System by means of a High-Level Interface (HLI), to provide operators and technicians with detailed status and alarm conditions regarding the UPS systems.

Due to the Centralized configuration, the following detailed diagnostic information is required, and shall be presented to the operator via a drop-down menu option within the SMS:

- UPS Data:

- Manufacturer

- Type

- Serial Number

- Software Version

- Battery Data:

- Battery Status

- Time Remaining in minutes

- Remaining Charge in %

- Battery Voltage

- Battery Current

- Battery Temperature in Deg C

- AC Input Data:

- Frequency per phase

- Voltage per phase

- Current per phase

- Power per phase

- AC Output Data:

- Frequency per phase

- Voltage per phase

- Current per phase

- Power per phase

- Load % per phase

- UPS Alarm Conditions:

- Battery Failure

- On Battery Power

- Low Battery

- Depleted Battery

- Over Temperature

- Input Supply Out of Limits

- Output Out of Limits

- Output Overload

- Bypass Active

- Bypass Inhibited

- Charger Failure

- Fan Failure

- Fuse Failure

- Diagnostic Test Failure

- Communications Failure

- Shutdown Pending

- Shutdown Imminent

All alarm conditions shall be presented to the operator within the Fault queue as described in the specification.

### System Configuration

The Interactive Security Management System (SMS) shall consist of multiple Operator Workstations, situated in the local, movement and central control rooms, and shall be networked by means of a Fibre Optic Large Area Network (LAN).  This network shall be a dedicated security network for use by the SMS only.

The network interface between control rooms shall be by means of a Fibre Optic medium, and shall form a star configuration from the Central Control room to each local control room to ensure local system autonomy.

All operator functions shall be controlled by means of a mouse, and shall require the minimum movement and actions in order to complete a required task.

The audio sub-system components within each control room shall form an integral part of the control console, and shall not require the use of external control equipment such as PTT buttons, Operator Keyboards etc.

All security sub-system control functions shall be interlocked to ensure that functional procedures are adhered to.

The following Interlock functions shall be programmed as an integrated function of the Security Management System:

- The selection of Cameras prior to Door opening

- The selection of Intercom communications prior to Door opening

- Automatic Camera select upon door opening

- Monitored door interlocking

- Automatic Camera selection upon Intercom activation

- Automatic Video recording on camera image activity

- Automatic event recording on individual operator activity

- Automatic Control console “LOG-OFF” on control room door

- Interlock capability according to operator log-in level

Alarm processing, alarm logging, alarm response data entry, graphical and text based user interface, data entry, and other system management functions shall be performed by the SMS operator workstations connected to the SMS network. The operator workstations shall be located in the Central Control Room and other nominated locations.

All Distributed control modules as other than door control modules mounted in door headers are to be suitably mounted within secure enclosures to the approval of the Engineer and located in the respective buildings' security and communications equipment cupboard, or other secure area as approved by the Engineer.

The SMS shall utilize a single global database and shall be fully distributed to Distributed control modules connected to the SMS security network. All system operators shall have limited access to this information/data from the operator workstations. The level of access shall be controlled by use of the Biometric logon site available at each operator workstation.

The system shall be designed such that failure of any control module or operator workstation shall not functionally affect the operation of any other module, network, building or Operator workstation connected to the SMS network.

Similarly, should any area lose power or suffer a loss in communications due to a break in the communications cabling, all Distributed control modules installed in that area shall continue to operate with no loss of functionality.

The SMS shall be fully programmable to allow:

- Response instructions to be displayed for all alarms types.

- Use dynamic (real time) graphics to display device status.

- Initiate operator commands via system tailored icons.

- Display building layouts in a graphical representation.

- Easy to follow menus with single key select options, to assist in the daily routine operations of each site.

- Allocate alarm priorities.

- Set Alarm response properties.

- Set lock/unlock and access/secure operating schedules.

- Generate User defined reports.

The contractor shall allow adequate time to liaise with the Engineer in order to detail any user specific requirements necessary for the operation of each building, system, alarm type, and alarm response configuration within the system. This shall include the configuration of maps, report formats, access schedules, alarm response instructions and the like, to suit each operator workstation.

The system shall be modular in design to allow for future system expansion with minimum cost and disruption to the existing operational system.

Tenderers are to specify the systems total capacity for future expansions.

Such upgrades shall not render a redundancy in field hardware, the Central Processing Units or any major component of software, firmware or operating systems.

### System Performance

#### Central Operator Workstations

The interaction delay between activating a control icon on any given operator workstation and the controlled point activation, (i.e., the lock), shall be no greater than one second (1 sec).

The interaction delay between controlled point activation and any given operator workstation response either by activation of an audible alarm and/or the associate icon changing state (color) shall be no greater than one second (1 sec).

The interaction delay between recalling any floor plan at any given operator workstation shall be no greater than one quarter of one second (0.25) second.

#### Local Operator Workstations

The interaction delay between activating a control icon on any given operator workstation and the controlled point activation, (i.e., the lock), shall be no greater than one half of one second (0.5 sec).

The interaction delay between controlled point activation and any given operator workstation response either by activation of an audible alarm and/or the associate icon changing state (color) shall be no greater than one half of one second (0.5 sec).

The interaction delay between recalling any floor plan at any given operator workstation shall be no greater than one quarter of one second (0.25) second.

### Minimum Hardware Requirements

#### Operator Workstations

- Logon Reader:	Vandal resistant Finger Print verification reader for automatic operator identification and logon.

#### Management Workstation

- A single Management Workstation shall be provided.

- Logon Reader:	Vandal resistant Finger Print verification reader for automatic operator identification and logon.

#### Server Workstation

- A redundant server configuration shall be provided.

### Minimum Software Requirements

The Security Management System (SMS) software shall be design specifically for Integrated Security Management Applications, shall have a proven track record in the security industry, and shall be an Off-the-shelf package available through a distributor network.  The off-the–shelf software shall be programmed and tailored to the specified functions and features described herein and as indicated on the accompanying drawings.

The software shall convey and accurate floor plan of all areas that require display on the VDU. The software shall utilize the maximum resolution and colours of the SVGA monitor to enhance and simplify the displayed control and status information. Fast orientation and ergonomics will be the goal of the graphic displays.

The software shall provide integrated Biometric (Fingerprint) log-on security functionality with security level protection for all Mouse driven operator workstations. The Biometric (Finger print) logon site shall be capable of providing a one too many search algorithm to confirm operator credentials, without the need for entering user details or the swiping of a personal identification card.

There shall be a minimum of ninety-nine (99) levels of access, and shall be expandable.

The software shall provide a user database within the Management workstation.  The database shall support a minimum of two thousand (2000) users.

The software shall provide on-line utilities accessed through the Management workstation menu structure. These utilities shall provide the system supervisor with the ability to edit and update required data bases, system operating variable, report configuration and generation, alarm tags and point descriptions, etc.  These utilities shall be protected by security levels and Biometric Access.

All software licenses shall be transferred to the Owner at completion of the project.  This shall include but not be limited to all original installation disks, software manuals, equipment manuals, etc.  All project specific applications software shall be transferred at the end of warranty period.

### Operator Visual Display Units

#### General

The SMS system offered shall be capable of providing a multiple operator workstation environment, which may be configured for full or selective operational & functional monitoring and control of select areas and functions.

Operator workstations shall be located as indicated in the tender drawings issued.

The operator workstations shall operate in both text and graphics based display. Any operator workstation enabled via the Biometric logon system shall be capable of controlling any area within the site providing the respective operator is authorized to do so.

The operator workstation shall also be capable of implementing changes to the system configuration and parameters, provided the operator has the necessary administration rights.

Entries, deletions or modifications to the configuration shall be possible via the operator workstation VDU/Keyboard without loss of, or degradation to, any other system functionality.

The following workstation functions shall be possible:

- Displaying point status information.

- Manually initiating control commands.

- Displaying system events and alarms.

- Displaying staff, visitor photographs for positive identification.

- Enrolling and verifying staff, visitor fingerprints. (Visitor Management module)

- Assigning operator access levels.

- Altering time schedules and creating new time schedules.

- Assigning or modifying time schedules for automatic operation of monitored doors/gates and redirection of duress alarms and indicators appropriate to the user's building/department/etc.

- Overriding time controlled functions, momentarily, to allow operator control of doors/gates/and the like.

- Altering existing or assigning new descriptions or actions.

- Displaying status of all alarm sectors within the user's areas.

- Remotely operate doors/gates within their restricted areas.

- Displaying all appropriate building activities.

- Performing on-line backup copies of complete system without any degradation in the overall system performance.

- Displaying building alarms including duress push buttons, etc.

- Enable the viewing of Sub-system status icons to be enabled or disabled through a built-in menu structure.

All of the above shall be restricted by user level based on the finger print access to the operator workstation.

#### Monitors

All operator workstations shall be of robust construction, ergonomically designed to minimize operator fatigue.

#### Keyboards

Keyboards shall be supplied with all workstations, however shall only be used for commissioning and maintenance purposes. All operator functions shall be performed by means of an optical mouse, with system screens being designed so as to require the minimum operator action. Functions such as audio system Push to talk, volume up and down control etc shall be possible by means of function keys on the SMS workstation.

#### Printer

A high-quality Inkjet printer shall be supplied, installed and commissioned as part of this contract, for use with the management workstation in order to generate user defined management reports.

The printer shall incorporate a visible control panel with LED indication for power on, paper out and ready.

The printer shall be installed and configured into the Management workstation to be installed within the Central Control Room.

The printer shall be supplied with both power and data cables of suitable length to suit the location. In addition, the printer shall be set up complete with one full box of paper and two spare ink cartridges each.

#### Mouse

All mouse devices shall be optical of robust construction and suitably secured by an interconnecting cable.

#### Networking

Each SMS workstation installed on the security LAN shall be capable of monitoring and reporting the current status of all workstations on the network.

Should communications between workstations or control equipment be disrupted, an alarm shall be generated at the Central Control Room Operator workstations to alert the operators of the failure within the communications network.

Alarms generated shall be displayed at the operator stations, while updating the system database with the Time, Date and relevant workstation detail.

Failure of any operator workstation shall not prevent communication between any other workstation or Distributed control modules and their associated devices.

### Software

#### General

Software shall be fully proven prior to being supplied, installed, tested and commissioned.

A list of reference sites at which the system software has been installed and operational at the date of the closing of this tender shall be provided.

The operator interface software shall incorporate English language descriptions and messages using both text based menus and graphical/icon displays. All configurations (e.g. entering of alarm response properties, adjusting time schedules, user data, etc) shall be performed on-line without effecting the operation of the overall system.

Selective access to different operator functions shall be configured based on an operator’s user level. User levels shall be determined from the Biometric verification each time an operator logs on to a workstation.

After any predefined period, if no operator activity has occurred at the operator workstations, that station shall automatically request Biometric verification failing which the station shall log off.

The time period before automatic logging off of workstations shall be user configurable, and shall be determined during commissioning of the system, in liaison with the Engineer.

#### Operating System

The operating system shall be a recognized and widely accepted standard operating system that shall suit the requirements of the system to be installed. The operating system shall be a real time multi-user/multi-tasking system such as Windows 10.

The operating system shall have proven and demonstrated reliable operation in the security environment.

Facilities shall be provided to store all programs on site and include all equipment necessary to backup and reload all system programs, including the operating system with all user specific system parameters.

#### System Access

Operators shall be required to "log on" to operator workstations using the finger print reader provided at each operator station before being able to access the system or user information, reset alarms or access any other system functions.

Access to all workstations shall be limited through allocation of access levels.

A minimum of 2000 users and 99 User levels shall be available. Only users allocated with a user level of 99 shall be capable of the assignment and changing of passwords to all levels.

Each operator shall be allowed to access different operator commands and functions, and view certain individually assigned events, menus and functions based on their assigned user level.

#### Scheduling

The SMS system shall have the ability to configure schedules which do not restrict the user to pre-determined times, dates or access levels. Access to and editing of these schedules shall be possible via the Management workstation.

The following schedules shall be configurable:

- Operator station Access times.

- Designated Alarm priority changes.

- Automated door locking/unlocking.

### Archiving Historical Data

#### General

Archiving of historical data shall take place automatically according to a configurable time frame, which shall be set via the Management workstation. The archived files shall be stored on the Raid 1 servers situated in the Central Control Room equipment rack. The system shall be capable of storing archived history files for a minimum period of 12 months.

Archived history files shall be read directly from the current or archived databases, without terminating or suspending the logging of current events.

#### Overwriting

The SMS software shall display an alarm to system operators warning of the imminent loss of archived data once the available disk space becomes full. The alarm shall occur with sufficient margin to allow the systems operator to execute a manual history file dump to the removable storage medium, if required (normally 80%). The percentage alarm set point shall be variable by the highest user level.

#### System Logging

The server workstations shall be capable of logging the following data:

Event related data:

| Item | Database Fields |
| --- | --- |
| 1 | Time and Date Stamp |
| 2 | Equipment Type |
| 3 | Control Area |
| 4 | Equipment Designation |
| 5 | Equipment Location |
| 6 | Alarm/Event Type |
| 7 | Alarm/Event Status |
| 8 | Responsible Operator |
| 9 | Operator Workstation Name |
| 10 | Control Area |
| 11 | Alarm/Event Priority |

Logged Events/Alarms:

| Item | Intercom Events/Alarms |
| --- | --- |
| 1.1 | Intercom Station Call in |
| 1.2 | Intercom Station Activated |
| 1.3 | Intercom Station I/O Failure |
| 1.4 | Intercom Station Tamper Alarm |
| 1.5 | Intercom Station Threshold Alarm |
| 1.6 | Intercom Station Fault |
| 1.7 | Intercom Call-in Transferred |
| 1.8 | Intercom Call-in Unanswered |
| 1.9 | Intercom Station Isolated |
| 1.10 | Intercom Station Isolated warning |
| 1.11 | Intercom System Hardware Failure |
| 1.12 | Intercom System Communication Failure |
| 1.13 | Intercom Alarm/Failure Acknowledged |
| 1.14 | Intercom System Call Central Command |
| 1.15 | Intercom System Call Movement Command |
| Item | CCTV Events/Alarms |
| 2.1 | CCTV Camera Activated |
| 2.2 | CCTV PTZ Preset Edited |
| 2.3 | CCTV Sequence Selected |
| 2.4 | CCTV Sequence Edited |
| 2.5 | CCTV System Hardware Failure |
| 2.6 | CCTV System Communication Failure |
| 2.7 | CCTV Alarm/Failure Acknowledged |

| Item | NVR Events/Alarms |
| --- | --- |
| 3.1 | NVR Channel Record Command |
| 3.2 | NVR Channel Halt Record Command |
| 3.3 | NVR System Hardware Failure |
| 3.4 | NVR System Communication Failure |
| 3.5 | NVR Alarm/Failure Acknowledged |

| Item | Door Events/Alarms |
| --- | --- |
| 4.1 | Door Open Command |
| 4.2 | Door Closed Command |
| 4.3 | Door Fault on Closing |
| 4.4 | Door Fault on Opening |
| 4.5 | Door Forced Open Manually |
| 4.6 | Door Open outside of limits |
| 4.7 | Door Open for extended period |
| 4.8 | Door Control module Communication Failure |
| 4.9 | Door DPS Opened |
| 4.10 | Door DPS Closed |
| 4.11 | Door Interlock Override Command |
| 4.12 | Door Group Activated |
| 4.13 | Door Group Edited |
| 4.14 | Door Emergency Release Activated |
| 4.15 | Door Control System Hardware Failure |
| 4.16 | Door Control System Communication Failure |
| 4.17 | Door Alarm/Failure Acknowledged |

| Item | Gate Events/Alarms |
| --- | --- |
| 5.1 | Gate Open Command |
| 5.2 | Gate Stop Command |
| 5.3 | Gate Close Command |
| 5.4 | Gate Fault on Closing |
| 5.5 | Gate Fault on Opening |
| 5.6 | Gate Forced Open Manually |
| 5.7 | Gate Open outside of limits |
| 5.8 | Gate Open for extended period |
| 5.9 | Gate Control module Communication Failure |
| 5.10 | Gate Alarm/Failure Acknowledged |

| Item | Boom & Spike Barrier Events/Alarms |
| --- | --- |
| 6.1 | Boom & Spike Barrier Open Command |
| 6.2 | Boom & Spike Barrier Stop Command |
| 6.3 | Boom & Spike Barrier Close Command |
| 6.4 | Boom & Spike Barrier Fault on Closing |
| 6.5 | Boom & Spike Barrier Fault on Opening |
| 6.6 | Boom & Spike Barrier Forced Open Manually |
| 6.7 | Boom & Spike Barrier Open outside of limits |
| 6.8 | Boom & Spike Barrier Open for extended period |
| 6.9 | Boom & Spike Barrier Control module Communication Failure |
| 6.10 | Boom & Spike Barrier Alarm/Failure Acknowledged |

| Item | Intrusion Events/Alarms |
| --- | --- |
| 7.1 | Intrusion Zone Activated |
| 7.2 | Intrusion Zone Alarm Acknowledged |

| Item | Panic Button Events/Alarms |
| --- | --- |
| 8.1 | Panic Button Activated |
| 8.2 | Panic Button Activation Acknowledged |

| Item | UPS Events/Alarms |
| --- | --- |
| 9.1 | UPS Mains Failure Alarm |
| 9.2 | UPS Load on Bypass |
| 9.3 | UPS Battery Low |
| 9.4 | UPS Battery Failure |
| 9.5 | UPS Load not protected |
| 9.6 | UPS Surge Arrestor Failure |
| 9.7 | UPS Communication Failure |
| 9.8 | UPS Alarm/Failure Acknowledged |

| Item | SMS Events/Alarms |
| --- | --- |
| 10.1 | New Operator Enrollment Successful |
| 10.2 | New Operator Enrollment Failed |
| 13.3 | Operator Details Edited |
| 13.4 | Operator Details Deleted |
| 13.5 | Workstation Logon Successful |
| 13.6 | Workstation Logon Failed |
| 13.7 | Workstation Unauthorized Access Attempted |
| 13.8 | Workstation Manual Logoff |
| 13.9 | Workstation Automatic Logoff |
| 13.10 | Workstation Inhibited |
| 13.11 | Workstation Re-instated |
| 13.14 | Workstation Online |
| 13.15 | Workstation Offline |
| 13.16 | Workstation Communication Failure |
| 13.17 | Workstation Alarm/Failure Acknowledge |

#### System Reporting

The SMS shall be capable of performing SQL queries to the current or archived databases on the server workstations, format the data into customized reports which shall allow for the following:

- Display of all relevant information on any individual alarm point including alarm point identification by device number and alarm point status.

- Display all alarm points in the system in alarm or normal condition, as a single log.

- Display all emergency procedures applicable to any alarm type with corresponding alarm response actions and locations, per alarm device.

Reporting details shall include:

- Alarm point status

- Alarm count per device.

- Alarm activity over a time period, selected by time and date.

- Display of selected alarm transactions based on alarm type and a calendar / time period.

- Display system operators login/out history

- Display all operator commands entered by any or all operators based on time/calendar interval.

### System Status

The SMS shall provide a menu option which, when selected, allows the system to display or print a list of current alarms, faults and conditions including the current fault conditions relating to SMS workstations, Distributes control modules, sub-system equipment hardware and associated devices.

In graphical display mode the system shall display maps of each building complete with all internal levels and shall indicate all systems equipment status (i.e. locked/unlocked; open/closed; secure/access; isolated/active; alarm; tamper etc).

### Current Alarm Window

The system shall provide an efficient and reliable alarm handling procedure and shall include both audio and visual annunciation, logging to the database and recording of the history file the device description, point description, location, time and date the alarm occurred.

The system software shall have the ability to route only selected alarms to specific operator workstations, allowing different locations or applications to be segregated on a building or system basis.

All systems activity shall be presented to ensure proper actions have been taken and that no alarm is left unattended for any lengthy period. Alarms, which have been acknowledged, and not cleared/reset shall be clearly distinguishable.

Upon occurrence of an alarm(s) a user configurable audible tone shall sound at the operator workstation(s) and display an indication of the incoming alarm together with its priority.

If there are additional alarms to acknowledge the operator’s station shall continue to sound the appropriate alarm tone, display the number of alarms waiting and identify the highest priority alarm.

The first alarm displayed shall be the highest priority alarm followed by the next highest priority alarm, etc.

All alarms are required to be separately acknowledged by the operator, by means of the mouse provided to acknowledge and reset each alarm separately.

Each time new alarms are created the system shall restack the alarms so the operator sees them in order of priority.

The system shall also have an alarm/event status display available to the operator at all times on the operator’s station.

The display shall be a real-time dynamic display of alarms in the active state, or system component failures.

An audit trail shall be used to log the actions taken by all system operators in response to an alarm. The audit trail shall note:

- When the alarm was activated.

- When the alarm was acknowledged.

- Who acknowledged the alarm.

- When the alarm was restored.

The system shall record every user command, acknowledgment and log every operator login.

These transactions shall be routed to the history database.

Any alarm point which has been suppressed/inhibited by the operator shall on expiry of the time zone, or when unsuppressed by the operator, generate an alarm if the alarm point is in the "active" state. The report to the operator terminal shall be the same as described above.

Each alarm point shall have the site for a description of the alarm occurring. A

Comprehensive outline for operator instructions, detailing all response actions shall be provided for all alarms.

### Graphical Display

The SMS shall support a minimum of 150 colour maps for the purpose of displaying the location and real time status of any SMS input or output.

Graphical maps to be included within the initial configuration are to show in detail the following areas:

Site plan showing all buildings and locations of all alarm points and operator workstations.

A plan of each accommodation unit and building.

All buildings devices/status/alarms and the like.

All building tamper, communications, power and the like devices/status/alarms and the like.

Other maps as required to clearly display all alarm input within buildings, or an external equipment cubicle locations.

Each site map shall be provided with a site plan key, which shall be common to all maps and situated in the same position. The key shall provide a means for the operator to quickly navigate through the entire site without the need to use standard navigation buttons or the main site map.

All device location and statuses shall be detailed on each map and coloured accordingly for ease of recognition of both the device type and real time status.

Text messaging identifying the device type, designation and alarm status shall be available in a “mouse over” or “windows hint” structure to minimize text on individual maps.

All text descriptors shall be approved by the Engineer prior to final acceptance. Liaise with the Engineer when programming these maps and other alarm/response descriptions.

Function key descriptions shall also be displayed as mouse over or windows hints.

Graphical map displays shall be of high resolution to enable accurate images to be represented. The configuration software shall provide a complete graphical design environment in order to design/edit building and site maps. A standard icon library shall be available to the designer in a window environment to enable efficient editing of existing maps by means of dragging and dropping equipment icons onto maps.

The system shall allow maps to be linked by means of navigation buttons to allow operators to "zoom" in or out to display either additional detail or an overall map.

Point status and locations shall be clearly displayed using colour-coded icons. All icons shall display real time status of each point with continuous updates being provided to any dynamic screen display.

Updates shall occur every 1 second or less. Icons shall be easily duplicated from a library of standard symbols at the configuration stage of developing the graphics.

### Security Management Functions

#### Configuration

The SMS shall consist of a multiple screen representation of the entire site, which shall contain all of the necessary icons to control all security sub system equipment and devices situated throughout the site. All icons shall be activated with the use of a mouse. All icons and status indicators shall be a minimum of 5mm in diameter. All symbols shall provide status by color and/or associated text.

#### Global Function Operations

Global function icons shall be located at the bottom of each graphic screen in the form of a footer window, which shall be common to all area maps. These icons, if active, shall control the global functions for the entire site.

##### System Control

Activating this icon shall cause the system to switch to the system control screen. The System Control screen shall provide a complete system diagnostic window for all sub-system components and communication systems within the entire site.

The diagnostic information shall include but not be limited to the following:

- UPS System (Per Zone):

- Load on Bypass

- Load not protected

- Mains Failure

- Battery Fault

- Battery Low

- Surge Arrestor Failure

- Control Hardware Status (Per Zone):

- TCP/IP communication Failure

- Control Network communication Failure

- Device Network communication Failure

- I/O Device Failure

- Communication Redundancy Integrity

- CCTV Matrix communication Alarm

- Perimeter Protection System (Per Zone):

- Intruder Detection Alarm

- Video Motion Detection Alarm

- Door position switch violation alarm per DPS

- Controlled door security violation alarm per door

- Fire door security violation alarm per door

- Panic Button activated alarm per Panic Button

- Intercom Call In Failure per Intercom

- Operator Log On Violation

Where applicable all alarm conditions shall allow for operator acknowledgement and automatic selection of the alarmed zone layout screen.

##### Site Plan

The site plan shall consist of an interactive miniature layout of the entire site, and shall be situated on the bottom Right hand side of each operator screen.

The site plan shall provide the operator with a quick method to access an individual area to monitor and / or control.

The site plan shall also indicate critical operational information to the operator, which shall include but not be limited to the following:

- Fire Doors Unsecured

- Sally port Doors Unsecured

- Local Control Room Logon Status

- Local Control Room Call In

- Local Control Room Communication Alarm

##### Volume Up

Activating and maintaining this icon shall result in an increase in the operator console speaker volume. The icon shall change status to RED to indicate activation of this function.

##### Volume Down

Activating and maintaining this icon shall result in a decrease in the operator console speaker volume. The icon shall change status to RED to indicate activation of this function.

##### Select

Activating this icon shall result in either the first audio call-in or the currently selected audio call-in in the Audio Call-in Queue to be answered. Upon answering the call, the call shall be removed from the Audio Call In queue on all workstations.

##### Reset

Activating this icon shall result in either the first audio call in or the currently selected audio call-in in the Audio Call-in Queue to be reset. Upon resetting the call, the call shall be removed from the Audio Call In queue on all workstations.

##### Push To Talk

Activating and maintaining this icon shall results in the PTT function being activated within the audio control hardware. Releasing the icon resets the PTT function.

##### Call Central/Movement

Each local operator workstation’s footer window shall contain a “Call Central” and a “Call Movement” icon. When selected the SMS shall generate a high priority call-in at the Central or Movement Control operator workstations. Central and Movement control room operators shall respond to these call-ins in the same manner as with a normal intercom station call request.

Movement Control workstations shall be equipped with “Call Central” functionality only.

##### Audio Call In Queue

The SMS footer window shall contain an Audio Call-in queue site into which audio call requests are entered on a first in first out (FIFO) basis.

Upon receipt of an audio call-in from any intercom station in the site, the call-in detail listing the control area, equipment designation and the specific location of the calling intercom station shall be entered into a FIFO queue.

The call-in priority of each Intercom station within the site shall be individually configurable within the SMS, and station priority shall take preference over the FIFO queue. Intercom station call requests of higher priority e.g. Control room call-in requests shall be entered into the top of the queue.

The following methods of answering calls-ins shall be possible:

- Highlighting the desired call-in in the Audio queue and clicking on the “Select” icon in the footer window.

- Clicking repeatedly on the “Select” icon in the footer window, which shall automatically answer the oldest entry in the Audio queue.

- Double clicking on any entry in the Audio queue.

Any of the above-mentioned methods of answering a call-in shall reset the currently selected intercom station and enable the selected station as well as simultaneously removing the entry from the Audio queue on all workstations.

When the local operator workstations are logged on, call-ins from the relevant local area  shall be directed to the local workstation. In the event that the call is not answered within thirty seconds, the call shall be forwarded to the Central Control room workstations. Call-ins from local areas in which a local operator is not logged in, shall be forwarded immediately to the Central Control room operators.

##### Fault Queue

The SMS footer window shall contain a Fault queue site into which all security sub-system or control system faults are entered in order of priority.

Upon receipt of any security sub-system or control system fault, the relevant fault detail including the control area, equipment designation and the specific location of the fault shall be entered into the Fault queue.

The Fault queue is intended to provide a quick reference to the system operator of current alarms, and is intended to replace functionality of the Current Alarm window described in the specification.

Faults may be dealt with in the following ways:

By right clicking on a specific fault in the queue, the operator shall be presented with an “Acknowledge” option. Clicking on the Acknowledge option shall enter the acknowledgement into the event recording system and remove the fault from the queue.

sBy double clicking on a specific fault in the queue, the appropriate area map shall be displayed with the faulty equipment control icon clearly visible. The equipment icon shall display the fault detail in a mouse-over or “hint” fashion. Right clicking on relevant equipment icon shall present the operator with an “Acknowledge” option. Clicking on the Acknowledge option shall enter the acknowledgement into the event recording system and remove the fault from the queue.

Local operator workstations shall display alarms and faults related to the immediate area of control only. Central operator workstations shall display all current alarms within the entire site.

##### Synchronized Clock System

All operator workstations footer windows shall contain a synchronized digital clock, which indicates the Date and Time in 24 Hour mode.  The accuracy of the synchronized digital clock system shall be within +- one (1) minute within a thirty (30) day period, and shall be synchronized with the management workstation within the central control room each hour on the hour.

##### Operator Logon Details

The SMS footer window shall contain the detail of the currently logged on operator including full name and authorized user level.

#### Locking Operations

##### Door Position status (Monitored Only)

There shall be a status icon for each monitored door to indicate the position of the door.  The status icon shall illuminate red when the door is unsecured and shall be green when the door is secure.

Each DPS icon shall provide mouse over or “hint” fashion detail of fault conditions relating to the equipment element as well as indicating the equipment designation.

A right mouse click over any icon shall provide the operator with an option to acknowledge an alarm condition as well as to view the engineering properties of the element provided the necessary user level is active.

##### Unlock Icon (Swing Door)

There shall be a single control icon with visual status indication for each controlled swing door lock. Activating the UNLOCK command shall apply power to the lock and activate the UNLOCK control cycle.  The associated status icon shall indicate red when the incorporated lock status switch indicates an unsecured state and green when the lock is secured. Each door icon shall provide mouse over or “hint” fashion detail of fault conditions relating to the door.

A right mouse click over any icon shall provide the operator with an option to acknowledge an alarm condition, to inhibit a door open command, or to view the engineering properties of the element provided the necessary user level is active.  Inhibiting a door open command shall change the icon colour to blue.

##### Unlock / Lock Icon (Sliding & Fire Doors)

There shall be a single control icon with visual status indication for each controlled sliding door control mechanism.  Activating the UNLOCK/LOCK icon shall either activate the UNLOCK cycle or the LOCK CYCLE of the mechanism in a toggle fashion.  The associated status icon shall illuminate red when the door is unsecured and green when the lock is secured. Activation of this icon whilst the associated door is in travel shall cause the door to instantly change its direction of travel. Each door icon shall provide mouse over or “hint” fashion detail of fault conditions relating to the door.

A right mouse click over any icon shall provide the operator with an option to acknowledge an alarm condition, to inhibit a door open command, or to view the engineering properties of the element provided the necessary user level is active.  Inhibiting a door open command shall change the icon colour to blue.

##### Open / Close / Stop Icons (Sliding gates)

There shall be three individual control icons with visual status indication for each controlled sliding gate. Activating the OPEN icon shall activate the OPEN cycle of the controlled device Activating the CLOSE icon shall activate the CLOSE cycle of the controlled device. Activating the STOP icon while the device is in the OPEN cycle or CLOSE cycle shall STOP the device. The associated status icon shall illuminate red when the locking device is unsecured and shall be green when the locking device is secured. Each gate icon shall provide mouse over or “hint” fashion detail of fault conditions relating to the door.

A right mouse click over any icon shall provide the operator with an option to acknowledge an alarm condition or to view the engineering properties of the element provided the necessary user level is active.

##### Emergency release:

An Emergency release icon shall be provided for each housing unit day room area, which shall be used to initiate an automated opening sequence for Perimeter and Exercise yard doors. The opening sequence shall be configurable within the SMS in order to provide the most efficient opening sequence.

Activating this icon shall cause a pop-up window to appear on top of the graphically displayed area. Located within this window shall be text explaining to the operator that the activation of this function shall result in all controlled doors in the corresponding area to be released under an emergency procedure. Also located within this window there shall be three icons namely “Open”, “Close” and “Cancel”. Activating the icon with the text “Open” text will activate the emergency open routine. Activating the icon with the text “Close” text will activate result in the same doors to simultaneously close. Activating the icon with the text “Cancel” shall remove the pop-up window and resume normal operation.

Once an emergency release routine has been activated the doors in the controlled area shall open and indicate an emergency condition by flashing the affected door icons in RED. The activation of the emergency close routine shall return the icon status to normal

.

##### Interlock Group Status

Activating a door lock icon that is part of an interlocked group of doors of which one or more doors are currently open, shall cause a pop-up window to appear on top of the graphically displayed area to indicate to the operator that an interlocked door is currently open and that the “Interlock Override” function should be activated to open the door.

Right clicking on the door icon shall provide the operator with an interlock lock group option, which when selected shall indicate each door contained in the relevant interlock group.

##### Interlock Override

Activating this icon shall enable the operator to override an interlocked door. The override function shall only remain active for 10 seconds.  Activating a door control icon while override is active shall cause the associated door to unlock or open.  When the override timeout limit is reached, the system shall return to normal operation.

During the active 10s period the Icon shall Flash RED to indicate activity.

##### Group Assign Icon

Activating this icon shall result in the door status icons of all doors in the corresponding Perimeter area to turn White. By toggling the door control icon whilst in the “Group Assign” mode shall toggle the door icon colour from White to Grey. A White icon shall indicate that the door is included in the controlled group, whilst a Grey icon indicates that it is not included in the group.

Upon activating the Group Assign icon for a second time the system shall return to a normal state and set the controlled door group into memory. Re-activation of the Group Assign icon shall cause the door control icons to indicate the current group assign status from memory.

##### Group Release:

Activating this icon shall cause a pop-up window to appear on top of the graphically displayed area. Located within this window shall be three icons namely “Open”, “Close” and “Cancel”. Activating the icon with the text “Open” text will result in the doors included in the Group Assign memory to Open. Activating the icon with the text “Close” text will result in the doors included in the Group Assign memory to Close. Activating the icon with the text “Cancel” shall remove the pop-up window and resume normal operation.

#### Intercom Operations

##### Audio Control – Intercom Icon

The SMS shall provide a control icon with visual status indication for each intercom station within the entire site.

The icons shall be used to initiate or terminate an audio channel between the relevant control room operator’s audio console and the selected intercom station.

Each Intercom station icon shall provide mouse over or “hint” fashion detail of fault conditions relating to the station as well as indicating the equipment designation.

The alarm detail displayed by the “hint” function shall include:

- Intercom station Tamper alarm

- Intercom station Threshold alarm

- Intercom station I/O alarm

- Intercom station Communications alarm

All alarm conditions shall be presented to the operator within the Fault queue as described in the specification.

A right mouse click over any icon shall provide the operator with an option to acknowledge an alarm condition, to inhibit an intercom station, or to view the engineering properties of the element provided the necessary user level is active.  Inhibiting an intercom station shall change the icon colour to blue.

- Intercom Station Call Up

Activating an intercom station icon shall open a talk path between the operator and the associated intercom station.  The associated status icon shall illuminate yellow to indicate an active channel.

Activating the intercom station icon a second time shall close the talk path and the status icon shall extinguish.

- Intercom Station Call-In

Upon activation of an intercom station call-in button located on the intercom station faceplate, the associated status icon shall illuminate and flash between yellow and grey with an audible tone. Activating the associated intercom station icon shall open a talk path between the operator and the staff station.  The status icon shall illuminate yellow and the audible tone shall silence.  Once complete, activating of the staff station icon a second time shall close the talk path and the associated status icon shall extinguish.

- Automatic termination of an audio channel

Should multiple audio call ins be received by the local operator, the operator shall only be required to select each audio icon once. The second icon selected shall initiate an audio channel to the appropriate intercom station and initiate an automatic de-select command to the previous channel.

- Delayed Call-In

Upon activation of an intercom station call-in button on an intercom station which falls under the control of a local control workstation, provided the particular operator is logged in, the call shall at first be routed to the local operator. If the local operator fails to respond to a call in within 60 seconds, the call is automatically routed to central control. This event is to be logged to the event recording system.

- Audio Queue

An Audio Call-in queue site shall be provided as an integrated function of the SMS system.

#### Closed Circuit Television (C.C.T.V.) Operation

##### CCTV. Fixed Camera Select

The SMS shall provide a single control icon with visual status indication for each CCTV Fixed Camera within the entire site.

Activating a camera icon shall cause the associated camera to be switched to the relevant operator’s spot monitor via the IP Interface to the CCTV Virtual Matrix. By selecting another camera icon the spot monitor image shall change accordingly.

Camera to Monitor commands shall be configured within the SMS to determine the allocation of spot monitors to operator workstations.

Currently selected camera icons shall illuminate RED, whilst un-selected icons shall illuminate GREEN.

Each Camera icon shall provide mouse over or “hint” fashion detail of the camera designation.

A right mouse click over any icon shall provide the operator with an option to view the engineering properties of the element provided the necessary user level is active.

##### C.C.T.V. PTZ Camera Select

The SMS shall provide a single control icon with visual status indication for each CCTV PTZ Camera within the entire site.

Activating a PTZ camera icon shall cause the associated camera to be switched to the relevant operator’s spot monitor via the High Level Interface to the CCTV Matrix. By selecting any other camera icon the spot monitor image shall change accordingly.

Camera to Monitor commands shall be configured within the SMS to determine the allocation of spot monitors to operator workstations.

Currently selected PTZ camera icons shall illuminate RED, whilst un-selected icons shall illuminate PURPLE.

Each PTZ Camera icon shall provide mouse over or “hint” fashion detail of the camera designation.

A right mouse click over any icon shall provide the operator with an option to view the engineering properties of the element provided the necessary user level is active.

##### C.C.T.V. PTZ Control

Once a PTZ camera icon has been selected by the operator, the SMS shall provide a pop-up control window, which shall allow the following PTZ control functions:

  - Pan Left

  - Pan Right

  - Tilt Up

  - Tilt Down

  - Simultaneous Pan Left, Tilt Up

  - Simultaneous Pan Right, Tilt Up

  - Simultaneous Pan Left, Tilt Down

  - Simultaneous Pan Right, Tilt Down

  - Zoom In

  - Zoom Out

  - Continuous rotate Left

  - Continuous rotate Right

  - Rotate Stop

  - Preset Position Select

  - Guard tour initiate

##### C.C.T.V. PTZ Preset Save

The SMS shall provide the operator with a menu option which shall initiate a pop-up control window, which shall allow the following PTZ control functions:

  - PTZ Camera Select (1-n)

  - PTZ Preset Select (1-99)

  - Pan Left

  - Pan Right

  - Tilt Up

  - Tilt Down

  - Simultaneous Pan Left, Tilt Up

  - Simultaneous Pan Right, Tilt Up

  - Simultaneous Pan Left, Tilt Down

  - Simultaneous Pan Right, Tilt Down

  - Zoom In

  - Zoom Out

  - PTZ Preset Store Command

  - PTZ Preset Load Command

The SMS shall be able to assign a specific PTZ Preset position to a standard fixed camera icon. The operator shall be able to click on a fixed camera icon, which shall load a PTZ preset position onto the appropriate spot monitor.

##### Sequence to Monitor Select

The SMS shall provide a single control icon with visual status indication for each Monitor within the individual control rooms.

A control room layout map shall be configured within the SMS, indicating the physical layout of the control desk and the CCTV monitors for the relevant SMS workstation.

The Monitor icon shall illuminate RED if a CCTV sequence has not been assigned to a specific monitor, and GREEN when a logical sequence has been assigned. The sequence number and description shall be displayed within the Monitor icon when a logical sequence has been assigned.

The operator shall be able to select the desired camera sequence by means of a Right mouse key function on the monitor icon.

Camera sequences may be assigned to any Monitor in the site including the spot monitors if required, however the manual selection of a camera image shall automatically override the sequence allocation.

##### Perimeter Detection - Black Screen Technology

The SMS shall provide integrated Black screen technology, which shall enable the automatic selection of relevant Perimeter Cameras to be allocated to Video Wall Monitors in the case of a Perimeter Detection alarm.

The SMS through its high-level interface to the Perimeter Detection, CCTV and NVR sub-system hardware shall make logical selections of camera images to the dedicated video wall monitors situated in the Central Control room.

Once a Perimeter alarm is triggered, the relevant zone fixed camera image shall be switched to the dedicated monitor along with the zone cameras on each side of the alarm zone.

The technology is required to ensure that all Perimeter alarm conditions are brought to the attention of the Central Control room operators immediately, and to present them with the necessary information to respond to the event.

The monitors to the left and right of the ALARM ZONE monitor ensure that an Intruder shall be visible should he/she move to the left or right of the immediate alarm zone. The PTZ preset position allows the operator to immediately view the alarm zone, and to follow the Intruder via the PTZ control functions.

### Visitor Management Module

The Access Control hardware provided shall support the Visitor Management System, which shall be provided as a fully integrated module of the Security Management System provided under this contract.

The Visitor Management System Module (VMS), shall provide for a fully integrated Biometric based Visitor, Staff identification System providing the following components as a minimum:

- Visit Booking

- Visitor, Staff Enrolment

- Visitor, Staff Verification

- Visitor, Staff location tracking

- Visitor Management

- Staff Management (Time & Attendance)

- Integration to Security Management System

#### System Components

The base system shall consist of the following components, however shall be indefinitely expandable to provide additional Visitor points, staff tracking points, as may be required.

- Visitor Enrolment stations (General or Visitors entrance gate).

- Visitor Verification stations

- Management Administration station (Administration building).

#### Component Description

##### Visitor Enrollment Station

The Visitor Enrollment Station shall consist of a dedicated PC workstation situated at the general or visitor’s entrance. The station shall consist of a PC, fingerprint reader, Camera, adhesive label printer and a storage tray for temporary Visitor cards.

The station shall be used to enroll visitor information into the system, and to print and issue a temporary Visitor identification card to each visitor, which shall contain the visitor details with a bar code for database indexing.

##### Visitor Verification Station

Visitor Verification stations shall be installed in each Visitor area e.g. Contact and Non-Contact Visitor, and shall consist of a PC workstation and a fingerprint reader.

The station shall be used to verify a visitor’s identity both upon entering and leaving the Visitor area.

##### Management Administration Station

The Management station shall be installed within the Administration building, and shall consist of a PC workstation, fingerprint reader, Camera, LaserJet reporting printer and a

Desktop Colour PVC identification card Printer.

The station shall be used to enroll staff members onto the system.

Staff members shall have their picture and fingerprints captured and shall be issued with a permanent staff access card, which shall be required to enter and leave the site.

#### System Description

In summary the objective of the system is to provide the following managerial functions within the site:

- The management and tracking of staff.

- The management and verification of Visitors and the recording of visits.

#### Typical Station Allocation

| Station Nº | Station Type | Building Allocation | Primary Function |
| --- | --- | --- | --- |
| 1 | File Server | Administration | Central file server (RAID 5 configuration). |
| 2 | Enrolment | Entrance/Gatehouse | Enrolment of Visitors Issuing of photo passes Adding to visitor count Search and display red list for banned visitors Login of Visitors to site Logout Visitors from site |
| 3 | Verification | Visitor | Positive identification of visitors in and out of the site. |

#### Installation Specifications

- Cameras to be wall mounted approx 1.8m from subject and above head height.

- If possible, natural daylight from behind camera provides the best illumination

- Plain or light coloured background (recommended –blue or light grey)

- Photographic strip lighting (white light illumination) to replace fluorescent strip lighting to eliminate yellow tones.

#### Environmental Conditions

The following environmental issues shall be taken into consideration:

- Temperature

To avoid overheating of the PCs, air conditioning equipment shall be provided.

- Humidity

The contractor shall ensure that the humidity shall be maintained within the manufacturer’s specification, and controlled via the internal air conditioning. The tenderer shall ensure the adequacy of the current air conditioning system, and make allowances to replace under rated units.

- Anti-Static

Adequate measures shall be taken to discharge any possible static at installation points. An installation specific survey with a list of recommended protection measures shall be required from the contractor.

- Power Supply

The system shall make use of a 240V AC source. The tenderer shall allow for a suitable uninterruptible power supply for each station capable of providing 35min of backup power.

#### Training

A comprehensive operator-training programme shall be provided, and shall cover all aspects of the Management system so as to provide first line local support to operators both operational and managerial.

The training shall include the following topics as a minimum:

##### Software

- System overview

- Pre-booking Visits Procedure

- Visits Orders

- Logging onto the System

- Enrolment procedure, and the understanding of fingerprint technology

- Verification Points and Procedures (In and Out)

- Red List Notification

- Visits Notification

- Visitor Enrolment

- Visitor Pass & ID Card Design

- System Maintenance

- Reporting and Enquiries

##### Hardware

- PC System

- Components and field replacements

- Access Control Terminals

- Printers & Print heads

##### Support

- Trouble Shooting Problems / Queries

- The Support Program and Support Procedures

- Support Communications

- Environmental Issues

### Maintenance and Spare equipment

The contractor shall provide 10% spares of all system modules, control modules, door modules including peripheral equipment, with a minimum of one modules of each type.

The contractor shall provide the Using Agency with the following:

- One printed copy of all application source code that is specific to this project, including comments; I/O lists, binding lists and a complete instruction document detailing the replacement of each module type.

- One copy of all application source code that is specific to this project in digital format (CD Rom or DVD). The files contained shall include both compiled and un-compiled source code.

- The contractor shall demonstrate that the un-compiled source code contained on the digital media is the current version of the code contained in the system modules.

- One system-programming device to facilitate control module replacement and/or expansion.

### Graphical User Interface

The following software functions are required as a fully integrated software module of the Security Management System provided as part of this tender.

The functions described are to be built in functions of the Security Management Operator Workstation software.

Due to the complex nature of the sub-system integration required by the system it is imperative that the Supplier of the Security Management System provides a direct interface (driver) to the sub-system hardware offered in this tender, and that the functions described below are in-built functions of the software.

#### Site Perimeter Map

A graphical presentation of the site perimeter shall include the following:

- Position of the perimeter

- Detection zones

- Gates

- Other static information (buildings or roads) that may be required to assist the operator to identify the location of an occurrence.

- The following Icons representing the alarm / maintenance status of field detection devices shall be included:

- Alarm status of taut wire detection for each zone.

- Alarm status of Delay Fence Integrity Detection for each zone.

- Tamper status of each field enclosure.

- The status of detection devices and status monitoring in the sally port area.

- The operational (maintenance) status of field equipment for each field controller.

Abnormal conditions shall be acknowledged by the operator by activating a single icon. This shall also stop the audible sounder.

The colour of status icons shall change in the following sequence.

- Green 	-	Normal condition

- Red Flashing -	New alarm condition

- Red Solid 	- 	Condition has been accepted by the operator

Blue shall indicate a device in a permanent abnormal condition and must be addressed by a maintenance repair procedure. Step 4 shall be omitted in case of certain maintenance devices or in case of CCTV surveillance where no field reset is required.

The following requirements shall be the minimum requirements for the user interface:

#### Operational Information

The following are shown on the operator interface:

- Site perimeter Layout

- Icons representing the alarm status of detection devices

- Indications of field node status and tamper

- Buttons to accept and reset alarms

- Buttons to issue a reason for alarms

#### Management Information

Operational Status

Parameters providing a summary of the operational status of the equipment including:

- Percentage site online

- Detection devices in inhibit status

- Status of worst case field node

- Condition of field communication network

System performance

Summary of the number alarms during a daily, weekly and monthly period. Alarms are categorized as the following types:

- Valid Alarms

- Nuisance Alarms

- Unknown Alarms

Operator performance

Values representing the maximum time the current and previous operator took to accept and reset alarms. Unattended time shall also be indicated.

Open a window to view the log

#### Diagnostic Information

The following diagnostic status information shall be made available:

- Real time Alarm status of all devices on the selected field node

- Maintenance status of these devices

- Buttons to inhibit any device

- Analogue values of detection devices

- Controls to adjust the operating parameters of field devices

### OPERATIONS AND INCIDENT MANAGEMENT SYSTEM

#### Scope

The contractor shall supply, install and commission a web based Operations & Incident Management system capable of integrating with the Security Management System offered with this tender. The OIM System shall be capable of extracting real time operational and maintenance related alarms and events from the Security Management Sub-system hardware, and to present this data to a dedicated OIM workstation to be installed in the Central Control Centre, as well as to relay the information in real time.

The OIM System shall provide a single dashboard overview of the various system components, to enable the user Department to determine at a glance where operational procedures are being ignored, are inadequate or require amending, as well as to determine the efficiency of Maintenance activities by Area, site or country wide.

The system shall be exception based, whereby trends are analyzed against a set of rules which can be configured per device. Only when the trend or activity for a device or sub-system deviates from the configured rules shall an Operational Incident or Maintenance Activity be generated and reported. Such Incidents shall be escalated to the appropriate levels according to a configurable escalation schedule.

#### 11.2	Integration

The OIM System shall be able to integrate with the following Security Sub-system hardware, as well as any additional hardware detailed in the site specific specifications under this tender:

      - Perimeter Detection System

      - Access Control System

      - Intercom

      - CCTV System

      - Intruder Alarm System

      - Uninterruptible Power Supplies

#### System Overview

The OIM System shall provide access to a Web based enterprise platform to capture and report data relative to incidents, investigations and exposure, providing a single dashboard view of any risk associated with the various hardware systems.

It shall be possible to intelligently action and query system data for risk, trending.  The system shall enable the user Department to make informed decisions which optimize performance and illustrate the effectiveness of it's security operation.

The system provided shall be capable of integrating with any commercially available Security Management System and Security sub-system hardware, and to present analytical data from all subsystems to the user on a single dashboard view.

The system shall have the ability to interactively manage incidents and investigations from beginning to end, including a complete sign off and review process.  Automatically generated notifications via email and SMS shall alert appropriate users to issues in real time.

The System shall be accessible by any number of users, from anywhere, at any time via thin client technology enabling the system to be accessed over the Internet, LAN or WAN through any secure connection. All data shall be SSL encrypted, providing secure data transactions, to enable users to log in remotely without compromising the system security.

The System shall enable users from multiple levels within the Department to access the same information for different reasons.

#### Functionality

The OIM System shall offer the following functionality as a minimum:

- Permissions

The OIM System shall have its own database security component to administer and control access to the underlying data. All users shall be granted access to the application by username and password, to allow strict control over the various levels that users are able to access. Generic username and passwords shall limit functionality, and shall be setup to cater for specific situations, for example where many different security personnel need to access, or enter data and where such personnel have not yet been designated and which may change on a day to day basis.

The system shall be capable of various levels of access, depending on the status of the user, for example, Management shall be able to view all outstanding incidents and investigation data, whilst others may be restricted to only those cases and investigations for which they are responsible. In addition, users shall be granted access to review certain aspects of a case but not to amend any of the details. The OIM Systems own Security shall be administered by users having specific administration rights, thereby allowing for the simple administration of existing and new user profiles.

- Reference Data

The reference data elements (i.e. locations, incident types, etc.) shall be treated as reference data items that shall be added as and when required by authorized users. This element of the application shall be tightly controlled to ensure that the referential integrity of data remains intact (i.e. reference data items cannot not be deleted, but merely flagged as “no longer in use”, and thus, not viewable from any of the drop down menus within the application).

- Incident Management

The system shall provide for two types of Incident entry. The first shall be an automated incident entry, whereby data received from the Security Management sub-system hardware e.g. an obstruction being placed in the path of a closing security door, shall be automatically entered and an incident created. The second type shall be a manual incident entry whereby users are able to enter incidents related to assets not connected to the Security Management System, e.g. an inmate reported as being in a restricted area without an escort.

An Electronic Occurrence Book/ Electronic Incident Book shall be a key component of the application and shall be available to build up a profile of various incidents (i.e. all related incident details such as an individual’, property, witnesses, vehicles, police case details, log file etc.) shall be reviewed as an extension of the incident.

Unique incident numbers shall be automatically established by the application, and once created, shall never be deleted to ensure integrity of the audit trail process. The incident shall become the primary source of input and all subsequent investigation activity shall be recorded as part of the incident.

New incident details shall be automatically entered or manually entered via a simple capture screen. It shall be possible to add specific details of the incident by the user. The capture of these details shall be standardized by means of pre-defined search lists to facilitate structured reporting (e.g. pre-defined incident types, locations etc.). Free form text input shall be limited to providing incident notes and wherever else it is considered necessary to cater for non-standard information situations. All entries into the application shall have standard time/date/user stamps for audit trail purposes. Incident details captured shall be validated as required to ensure that a minimum required level of detail is captured.

It shall be possible to select the incident complainants and any associated suspects from an existing list, or added at the time of creating the incident. Advanced search functionality shall allow a user to search across a number of search criteria (e.g. by surname, id number, name etc.) to ascertain whether the complainant or suspect already exists in the database. Mandatory procedures shall be automatically displayed in a popup window when specific incidents occur, to enable Control Room staff to follow a strict course of action when required.

- Investigation

Subsequent investigations of an existing incident shall be treated as adding additional data to the original incident profile. Only authorized users shall be able to add and amend investigation data. It shall be possible for management to view investigation data, and to be able to add additional comments or issues that need to be followed up.

It shall be possible to conduct an investigation into the following incident categories as a minimum:

1.	Security Incidents

2.	Maintenance Incidents

3.	Health and Safety Incidents

4.	Human Resources Incidents

System prioritized incidents shall be automatically assigned to the investigations database, however, it shall be possible for authorized users to override non-prioritized incidents and flag them for investigation if necessary. Users assigned to an "Administrator" security level shall be able to create “auto assignment rules” which shall automatically assign repetitive type investigations to relevant users without the managers input.

It shall be possible for Investigation managers to be presented with an incident summary once they log in to the system, which provides a prioritized list of investigations which have been assigned to them for review.

- 11.4.5	Reporting

The system shall provide a range of standard and pre-defined reports, with the ability to create user defined reports on an ad-hoc basis, where users shall be able to specify report parameters at the time the report is generated.

It shall be possible to generate the following report types as a minimum:

- Trending/ Graph Report

- Statistical Report

- Management Dashboard Report

- Map Report

All reports shall be web based, with the ability to export to Microsoft Excel or PDF format. The Management Dashboard Reports shall be dynamically linked to the database, displaying any criteria that the user wishes to view.

- 11.4.6	Data Search

The system shall provide the ability to cross reference between all incidents and related occurrences. The database shall be designed in such a way that the relationships between the various elements are automatically established at the point of entry, to provide advanced web based cross referencing of reports.

- 11.4.7	Equipment and Asset Register

The system shall provide a National equipment and asset register, which shall enable users to capture the details of any asset or piece of equipment on any of the sites linked to the National Control Centre. It shall be possible to create or edit an entry either from the relevant site or from the National Control Centre.

It shall be possible to Categorize and sub-categorize assets to three levels as a minimum, and provide the following Main Categories as standard:

- Security

- Electrical

- Mechanical

- Building

The following Sub-Categories shall be provided as standard

- Security

  - Perimeter Intrusion Detection

  - Security Doors

  - Access Control

  - Intercom

  - Public Address

  - CCTV

  - Intruder alarm

- Control Room Equipment

  - IT Equipment

  - Ancillary Equipment

  - Radio Equipment

  - UPS

  - Power Distribution

  - General

- Electrical

  - Lighting Fittings and Fixtures

  - Power Outlets and Switches

  - Distribution Panels

  - Cable and Wire-ways

  - UPS

  - Standby Generators

  - High Tension Equipment

  - General

- Mechanical

  - HVAC

  - Air conditioners

  - General

  - Lifts

The system shall provide for the seamless integration of all Security related assets into the OIM System Asset Register, by means of an automated import tool, which shall enable the Security Management System to automatically populate the OIM Systems Asset Register database with the following fields as a minimum:

- Category (e.g. - Security)

- Sub Category 1 (e.g. - Security - Door Control)

- Sub Category 2 (e.g. - Security Door Control – Swing Door)

- Site Reference

- Area Reference

- ID Number (Unique per asset)

- Bar Code Number

- Manufacturer

- Manufacturer's Part Number

- Description

- Distributor Name

- Distributor Telephone Number

In addition to the automated import facility, it shall be possible to view and manually edit the details associated with any imported asset as well as to manually create new assets and populate the database in accordance with the above-mentioned fields.

The system shall provide a standard .csv import tool for all other categories of assets not forming part of the Security Management System. The tool shall allow the user to create their own asset register in Microsoft Excel for the Electrical, Plumbing and Building related assets, and to import these spreadsheets into the OIM System via the CSV import tool provided.

The tenderer shall allow sufficient man hours for training of a suitable competent representative of the user, to enable them to create the necessary spreadsheets in preparation for importing into the system themselves.

- Planned Preventative Maintenance Module

The system shall provide a full Planned Preventative Maintenance module which shall enable the End User’s maintenance division to configure the Planned Preventative maintenance schedules for each asset type. As an example it shall be possible to schedule a routine maintenance activity for each individual asset by configuring a single asset sub-category type.

(i.e. all Security Door Controllers are to be serviced once every six months).

Once the service intervals have been entered per asset type, the system shall automatically generate the Annual maintenance schedule for each individual asset as well as to generate the daily schedule maintenance tasks for the assigned resources.

The following fields for the planned preventative maintenance schedules shall be provided within the OIM Systems database as a minimum:

- Category (e.g. - Security)

- Sub Category 1 (e.g. - Security - Door Control)

- Sub Category 2 (e.g. - Security Door Control – Swing Door)

- Site Reference

- Area Reference

- ID Number (Unique per asset)

- Bar Code Number

- Manufacturer

- Manufacturer's Part Number

- Description

- Maintenance procedure (Text field describing the maintenance procedure)

- Assigned Resource (e.g. - Team or Individual)

- Cycle (Annual, 6 Monthly, 3 Monthly, 2 Monthly, Monthly, Weekly, Daily)

- Estimated service time

When changes are made to a specific asset's Planned Maintenance criteria, an option shall be generated to apply the same criteria to all assets within the same Sub Category or ID Type. (Apply to all function). As an example, if the manufacturer of a specific door controller revises their recommended service period, the user need only edit the "Cycle" field of one such device, which can then be applied to all products within the same site with a single click.

Planned Maintenance Schedule Report

The system shall automatically generate a daily Planned Maintenance schedule report for each resource to which tasks have been assigned. The following information shall be provided per daily report as a minimum:

- Site Reference

- Area Reference

- ID Number Range (display each unique ID number to be serviced that day)

- Asset Description

- Maintenance procedure (Text field describing the maintenance procedure)

- Cycle (Annual, 6 Monthly, 3 Monthly, 2 Monthly, Monthly, Weekly, Daily)

- Scheduled Start Date

- Scheduled Completion Date

- Scheduled Time for completion

- Actual Time Completed (Manual entry by resource)

- Actual Time required (Manual entry by resource)

- Assigned Resource (e.g. - Team or Individual with space for signature)

- Resource Comments (Technician's description of the fault)

- Spares utilized (Technician's description of parts used)

Upon completion of scheduled Maintenance tasks, the system shall allow for all information which had been filled in on the printed report by the Technician and Administrative assistant, to be entered into the system and recorded in order to provided statistical reports relating to the predicted and actual time required to complete a group of maintenance tasks. The system shall use such information to prompt the appropriate user to amend Estimated service time per asset type,, in order to more accurately predict resource allocation.

- Automated Breakdown Notification Module

The system shall provide a fully configurable Breakdown notification system whereby breakdown related events can be created, edited or deleted as required. Events affecting the smooth operation of the Security Management System shall be automatically reported to the appropriate specialist sub-contractor via SMS and email in order to minimize the downtime related to the breakdown.

The following maintenance related events shall exist within the system as standard, and reported via SMS and email together with the date and time of the event and the breakdown category:

- Security Doors (Included, but not limited to)

Item	Security Door/ Gate Events

- Door Fault on Closing alarm exceeding limit

- Door Fault on Opening alarm exceeding limit

- Door Control Node Communication Failure (with module No. notification)

- Door Control Bus Segment Failure (with Bus segment No. notification)

- Door Control Area Controller Failure (with controller No. notification)

- Monitored DPS Open for longer than the configured time

- Intercom (Included, but not limited to)

Item	Intercom Events

- Intercom Tamper Alarm (with Area and Door notification)

- Intercom Node Communication Failure (with Node No. notification)

- Intercom Bus Segment Failure (with Bus segment No. notification)

- Intercom Area Controller Failure (with controller No. notification)

- Intercom Call Button wiring fault (with station No. notification)

- CCTV & Digital Recording System (Included, but not limited to)

Item	CCTV & Digital Recording Events

- Camera Signal/Image loss Alarm (with camera No. notification)

- Camera Communications Failure Alarm (with camera No. notification)

- NVR Communications Failure Alarm (with NVR No. notification)

- NVR Proprietary Alarm (with NVR and Alarm No. notification)

- Perimeter Detection System (Included, but not limited to)

Item	Perimeter Detection Events

- Kinematic Maintenance Alarm (with zone and sensor No. notification)

- Kinematic Loop Alarm (with node and Loop No. notification)

- Field Node communication Alarm (with node No. notification)

- Field Cabinet Tamper Alarm (with cabinet No. notification)

- Field Node Battery Charger Alarm (with node No. notification)

- Kinematic sensor Inhibit Alarm (with zone and sensor No. notification)

- Kinematic Loop Inhibit Alarm (with zone and loop No. notification)

- UPS System (Included, but not limited to

Item	UPS System Events

- UPS Mains failure (with unit No. notification)

- UPS Maintenance Alarm (with unit No. notification)

- UPS Load on Bypass (with unit No. notification)

- UPS Battery Low (with unit No. notification)

- UPS Battery Failure (with unit No. notification)

- UPS Load not protected (with unit No. notification)

- UPS Surge Arrestor Failure (with unit No. notification)

- UPS Communication Failure (with unit No. notification)

- UPS Room Door Open Alarm (with room No. notification)

- UPS I/O module communications Alarm (with module No. notification)

- UPS I/O Input wiring fault (with module and Input No. notification)

- Equipment Cabinets ( Included, but not limited to )

Item	Equipment Cabinet Events

- Equipment Cabinet Open Alarm (with area and cabinet No. notification)

- Equipment Surge Arrestor Failure Alarm (with cabinet No. notification)

- Ethernet Switch Communication Alarm (with switch No. notification)

- Security Management System (Included, but not limited to)

Item	Security Management System Events

- Server Communication Failure (with Server ID notification)

- Workstation Communication Failure (with WS ID notification)

- 11.4.10	Operations Monitoring Module

The system shall provide an Integrated Operations Monitoring Module, whereby the standard conditions of operation of Security Sub-System hardware can be defined, and monitored in real time, and to automatically report any deviation from the standard operating conditions. As an example, it shall be possible to create a standard operating condition (set of rules) for the operation of a Security Sliding Door, in which the user can define the period for which the door may remain unlocked (open) before an exception event is generated. In addition to the open time period, the user shall be able to define the number of such events per door, that would constitute an incident, and to automatically report the incident to a senior level within the system.

The logging and reporting of such incidents shall include all details relating to the event, for example, the Time, Date and Operator responsible for opening the door.

It is a specific requirement of this tender that the OIM System and the Security Management System (SMS) are fully integrated to enable operational incidents to be monitored and reported in real time.

The system shall allow system user's with a suitable security and experience level, to create user defined operational conditions for any security sub-system hardware component.

The system shall enable senior users to configure which alarms and events are to be escalated and to whom they should be reported.  The system shall also allow for general notification whereby senior users can be notified of Alarms and events without needing to take any action.

The system shall present the appropriate users with the following information relating to each alarm or event, via their Dashboard overview:

1.	Date of the incident

2.	Time of incident

3.	Category of Incident

4.	User responsible for the incident

5.	Responsible Users contact details

6.	Time lapsed since the incident

7.	Description of the Incident

8.	Recommended Action to be taken

- Dynamic Reports and Forms

The system shall provide a dynamic Reports and Forms tool, which shall enable users to dynamically create new pages (Tabs) and Input Fields for any additional information capture requirements. The tool set shall negate the need for Hard Coding Development and shall be carried out by a System Administrator.

## ACCESS CONTROL SYSTEM

### Access Control Management System General Description

#### General

The Access Control System, hereafter referred to as the “ACS”, shall provide the primary management interface for maintaining and managing the Organisations Security Centre. The “ACS” shall provide the integration backbone for connection to multiple 3rd party systems for monitoring and controlling security within the organisation without compromising on its primary function of true Access Control. The “ACS” shall provide be the data collection mechanism whereby all security data related to the secure functioning of the organisation shall be collected in an industry standard Firebird or SQL-based database.

As an Access Control System, the “ACS” shall provide the following features:

- The “ACS” shall provide the ability to control up to 256 Access Control Sites.

- The “ACS” shall provide the ability to control up to 64 System Controllers per site, hereafter referred to as locations.

- The “ACS” shall provide the ability to control up to 300,000 users per site. “ACS” system users shall hereafter be referred to as tag holders.

- The “ACS” shall ensure that Fingerprint Biometric Readers are an option.

- The “ACS” shall provide the option to implement Daylight Savings Settings per site.

- The “ACS” shall provide the option to implement Anti-Passback on single access points, or on user defined groupings of access points, hereafter referred to as zones.

- The “ACS” shall provide the option of limiting the number of users in an Anti-Passback zone.

- The “ACS” shall provide the option of multiple reader types at each location. These options shall include, but not be limited to:

- Fingerprint Biometric Readers

- Tag Readers

- Keypad readers

- Harsh Environment Metal readers

- 3rd Party card readers

- The “ACS” shall provide the option of setting individual reader modes at each access control reader. These modes shall include, but not be limited to:

- Biometric Only ( 1:to Many – Identification Mode)

- Biometric + 2nd Factor (TAG and/or PIN)

- TAG only mode

- TAG + PIN mode

- TAG + REASON CODE mode

- Personal Access Code mode

- Locked Mode

- Unlocked Mode

- Emergency Mode

- The “ACS” shall provide the option of single tag use, or multiple tag use per location.

- The “ACS” shall provide an interface for the administration of tag holders.

- The “ACS” tag holder interface shall provide the ability to assign up to 8 tags per tag holder.

- The “ACS” tag holder interface shall provide the option of linking up to 10 access groups to a single tag.

- The “ACS” tag holder interface shall provide the option of assigning access groups across multiple sites in the “ACS”.

- The “ACS” shall provide the ability to configure up to 10 000 Access Groups per site.

- The “ACS” shall provide the ability to configure up to three combinations of Time Pattern and Allowable Access Doors (Areas) per Access Group.

- The “ACS” shall provide the ability to configure up to 512 Access Time Patterns per site.

- The “ACS” shall provide the ability to configure up to 1024 Areas per site.

- The “ACS” shall provide the ability to generate multiple Time Triggered Actions per site.

- The “ACS” shall provide the option for defining Holidays whereby access rights can be denied or granted based on a tag holders individual access groups.

- The “ACS” system shall provide support for Vehicle control using RF technology, and user configurable Elevator control. Elevator control shall support up to eight elevators to a maximum of eighty floors per elevator

#### “ACS” Concept

The “ACS” system shall provide general access control for employees, as well as visitors. This shall be facilitated by the creation of doors, access groups and tag rights assignment.  The underlying architecture of the “ACS” shall be one of EVENTS and ACTIONS.

An event is defined as a ‘pre-defined system condition’. An example of a system event is an ‘allowed normal’ transaction or an ‘Input Alarm’ transaction that the “ACS” system controller recognizes in its database of events. The “ACS” controller shall recognize a range of events that include, but are not limited to the following categories:

Tag transactions – Allowed, Denied, APB, Zone, location, Time, suspended, blacklisted, Special, Reason code, Duress etc.

Zone monitoring Transactions – Zone Full, Empty, Not Empty, etc.

Location monitoring Transactions – Location locked.

Input Alarm transactions – Input triggered.

Door Sensing transactions – Door Forced, not opened, opened normally, open too long, closed, etc.

“ACS” hardware transactions – timeouts, power ups, etc

Time based event.

An Action is defined as a ‘physical capability of “ACS” hardware components’. The “ACS” components include Relays, buzzers and LED’s, as well as software defined multiple action components.

Each “ACS” hardware device shall have system defined default actions. The “ACS” software shall provide the administrator with the ability to create custom actions for each individual hardware component. The default, as well as user defined actions shall be configurable by duration. LED components shall be configurable by duration and LED colour. The Relay components shall be configurable by relay duration. The buzzer components shall be configurable by duration and buzzer tone and volume.

The “ACS” system controllers shall constantly monitor the system for the occurrence of any “ACS” event that occurs. When the event occurs, the “ACS” system controller shall trigger up to five user defined actions for the specific event that has occurred. These actions shall include, but not be limited to a combination of:

- Relay Actions

- LED Actions

- Buzzer Actions

- Multiple Actions

All system events shall be stored in the “ACS” database with date/time stamps.

In the case of Time Based events, the “ACS” controllers shall trigger actions based on specific times, once off, or recurring.

#### Software

The “ACS” software shall be written in an industry standard 4th Generation Programming Language. The “ACS” software shall be Client/Server in design. The “ACS” database shall be open in nature, allowing for simple integration with 3rd party software packages. There shall be two database vendor options available – An industry standard Open Source database, with its relevant database management systems (DBMS) tools, or an industry standard proprietary DBMS.

The “ACS” software shall be modular in design, providing the option of installing the respective modules on multiple client workstations across an organizations network. The “ACS” software shall also be able to run on a single workstation.

The “ACS” software shall make use of simple, easy-to-navigate graphical user interfaces that make use of either a drill-down tree structure, or a menu driven option.

The “ACS” software shall provide a Configuration module that allows for the complete configuration of the “ACS” including the setup of “ACS” hardware, “ACS” tag holders including Fingerprint Biometric template management and all “ACS” functionality.

The “ACS” configuration module shall also provide a software operator security module that provides the “ACS” administrator the option of configuring user profiles and creating user groups. The Operator Security module shall enable the administrator to provide granular access control rights to applications as well as access to tree structures, menus, and popup menus.

A separate database engine module shall facilitate the upload of system parameters and tag holder data to the “ACS” hardware and fingerprint template distribution to the fingerprint readers, whilst at the same time providing a separate downloader thread for download of all system related transactions from the “ACS” Hardware. The database engine module shall provide advanced connectivity options for configuration of multiple connection mediums, as well as an automated database backup site that shall backup the “ACS” database to a specified network drive. The “ACS” database Engine shall create an offline transaction file on the local workstation if the Network connection to the database is lost.

During initial system setup, or any subsequent system setup, the “ACS” database engine module shall provide the functionality to Auto identify new devices connected to the system. The “ACS” database engine shall interrogate the devices for their unique serial numbers and device type, and auto-assign logical addresses to each hardware device. The “ACS” database engine shall also populate the “ACS” database with the information previously gathered during the Auto Identification process. This information shall be viewable and configurable in the “ACS” configuration module.

The “ACS” software suite shall provide a Graphics module that allows software users to view, in real time, all “ACS” system related transactions. The Graphics module shall provide a transaction viewer module that shall report on all Access transactions, Alarm transactions and Message Protocols that are triggered by the software user. The Graphics module shall provide the graphics user to view 2 dimensional images of the entire “ACS” site, as well as 2-D images of all floor plans for the site.

The “ACS” software suite shall provide a tag holder administration module that shall enable the system administrator to separate tag holders into Employee groups and Visitor groups.

The “ACS” software suite shall provide system administration utilities including, but not limited to the following; A firmware upgrade utility that provides technicians the ability to upgrade and troubleshoot a faulty installation, A database archive utility, An Ethernet device configuration utility and a CSV import utility.

The “ACS” software suite shall also provide modules that enable communications with 3rd party systems including, but not limited to the following: Industry Standard Fingerprint Biometrics devices, Intrusion alarm systems and Digital Video Recording Systems (CCTV).

The “ACS” software shall also include all relevant configuration manuals in industry standard format.

The “ACS” shall provide a web-based reporting structure that negates the need for additional software to be installed on client workstations. Software users shall be able to connect to the Web-Reports via a standard Web Browser such as Microsoft Internet Explorer, or the open source Mozilla.

#### Hardware

- The “ACS” hardware architecture shall be Client/Server in nature with local door readers relying on System controllers to make all system related decisions.

- The “ACS” shall support a maximum of 64 System controllers per site.

- The “ACS” system controllers shall be regularly polled by the Database Engine Module to download “ACS” transactions to the system database and to upload relevant “ACS” configuration data to the system controllers. The “ACS” system controllers shall be able to run in a true offline mode when the “ACS” database engine module connection is not present.

- The “ACS” system controllers shall buffer up to one million system transactions per controller in the event of a loss of connection to the “ACS” database engine. Once the connection is re-established, the “ACS” system controllers shall automatically dump the system transactions to the “ACS” database. T

- The System controllers shall each be capable of controlling up to 32 Access control terminals, (64 IP Addresses) which shall include all, or a combination of the following devices: Door Controllers with their respective readers, 3rd Party Interface Door Controllers, Digital Input boards, Relay Extension boards, Fingerprint Biometric Readers, Time & Attendance Readers, Radio Frequency (RF) and Long Range Readers.

- Optional to the standard door controllers, the “ACS” hardware shall include Intelligent Door Controllers that shall allow access to the 2000 most recent tags used at the door in the unlikely event of a communications bus failure.

- The “ACS” Systems Controllers shall provide multiple connectivity options including, but not limited to RS485 and 10/100 Ethernet.

- All devices that connect to Systems controllers, hereafter referred to as terminals, shall connect to the Systems controllers via an RS485 connection port on the System Controller.

- The Fingerprint Biometric readers must connect via 10/100 Ethernet.

- The “ACS” System Controllers shall report any offline terminals without delay.

- The “ACS” terminals shall provide a combination of the following user-configurable components for use in the day-to-day operations of the “ACS”: Dry contact relays, Light Emitting Diodes (LED), Multi-function Digital inputs and 3rd party interface ports.

- The “ACS” door readers shall support either industry standard 125Kz proximity tags, or the 13.56 Mhz frequency Mifare tags. Door readers shall connect to the “ACS” via standard “ACS” door controllers, or the “ACS” 3rd Party interface boards. 3rd Party Door entry devices such as the Fingerprint Biometrics shall connect to the “ACS” via the 3rd Party interface boards.

- Door Readers shall support either proprietary system protocols, or industry standard Wiegand protocols.

- Door readers shall support the following or a combination of the following components that clearly indicate ingress or egress transaction approval or denial: Software configurable Bi-Colour LED and software configurable buzzer.

- The “ACS” software shall be capable of initiating protocol commands directly to the “ACS” hardware through the “ACS” database engine via user selectable messaging ports, through the Graphics module or through the “ACS” configuration module.

#### Integration

- The “ACS” system shall provide the backbone for various 3rd Party product integrations. Such integration shall include interfacing to various 3rd Party hardware vendors as well as software integration to multiple software vendors and systems.

- The “ACS” shall provide 3rd Party terminal ports on specific door controllers whereby multiple technologies can be connected to the “ACS”. These technologies shall include, but not be limited to: Fingerprint Biometrics Devices, Mifare Readers, Wiegand Readers, Bar-code readers and Radio frequency (RF) devices.

- Additionally, the “ACS” software shall comprise modules that connect to, and upload and download data from 3rd Party monitoring products. These products shall include, but not be limited to the Ziton ZP3 and ZP5 Fire Monitoring Panels, The Caddx Intrusion Alarm Systems, Biometrics Engines and the following selected IP Video Recording systems.

- Milestone

- Bosch

- Avigilon

- GeoVision

- Samsung

- iNet/Mirasys

- These systems shall integrate at the protocol level and communications across the multiple systems shall be seamless.

- The “ACS” database shall provide the option for integration to 3rd Party software modules, including, but not limited to: Human Resource Systems, Time and Attendance systems, Enterprise Resource Planning (ERP) systems, Supply Chain Management (SCM), Customer Resource Management (CRM) and Estate Management Systems.

- The “ACS” system shall provide the option to pass the Access Request from the “ACS” to one of the higher level systems for primary approval of the Access Control request. This ‘Host Validation’ shall occur seamlessly and without delay.

- The “ACS” system vendor shall be able to provide API’s, Database Schemas and ‘Best Practice’ guidelines to systems integrators.

- The “ACS” system shall provide user configurable ‘open’ TCP socket ports in its “ACS” database engine software to allow authenticated applications to monitor Access transactions, Alarm transactions and to perform real time door monitoring. There shall also be ports available for protocol messaging to “ACS” hardware, enabling 3rd Party systems to generate “ACS” actions on the system in real time.

#### Architecture

The “ACS” shall have a distributed processing architecture consisting of hardware, software and a system database.

## Key Elements

### Hardware

Hardware components of the “ACS” include System Controllers, Terminals, Readers, Tags, communications buses, and other components required for operation.  For detailed requirements, refer to the Hardware section.

### Software

Includes the software package used to configure the site or sites, add, delete and edit tag holders, and monitor hardware.  For detailed requirements, refer to the Software section.

## People

People using the “ACS” shall fall into two groups:

System Users

These are the installers, administrators, and technicians who work on the “ACS”

Tag Holders

These are the people who have access to Sites permanently or temporarily, where the “ACS” is installed

Note:

Tag Holders are not limited to people.  Any non-human object using a tag , Fingerprint Biometric reader or remote transmitter is effectively a tag holder.  For example, a vehicle can also be regarded as a tag holder.

## Interaction

The hardware is required to physically provide access control to an installation.  Software shall communicate effectively with the hardware to ensure efficient access control.  The hardware and software shall be designed to provide intuitive, fool-proof operation and interaction with people.

#### Features

## Access control

The specified system shall provide full advanced access control, with the following additional features:

## Building Management

Emergency Mode – when activated, pre-selected doors shall be opened automatically

Alarm Mode – when a security or fire alarm is activated, a signal shall be received by the “ACS” and system configured actions shall be triggered.

- Time Triggered Actions – specified actions are activated at specified times

- Event Triggered Actions – specified actions are activated when a specified event is detected

## Time and Attendance (TA)

The “ACS” shall provide suitable hardware and software, and integration tools to facilitate a TA subsystem.

## Anti-Pass back (APB) Control

The “ACS” shall have a site to set a Relaxed or Strict APB status per location or grouping of locations.

## Security

The “ACS” system shall provide high levels of physical security by ensuring the following basic principles:

Robust hardware – The “ACS” system shall provide, as it’s means of transaction collection, high quality, robust readers and peripheral devices.

Tamper proof hardware – The “ACS” hardware shall incorporate Tamper-switches on System Controllers, and high risk terminals, and the “ACS” software shall report any alarms generated on “ACS” hardware.

Secure software – The “ACS” software shall provide the option to implement operator security on all “ACS” software modules.

## Monitoring

The “ACS” shall provide the ability to assign designated users certain monitoring roles.  These users shall have access the “ACS” software to monitor transactions, alarms, and tag-holders, but shall not be able to make configuration changes.  Monitoring modules shall include a Graphical Floor plan monitoring module and a text based Transaction module. The aforementioned modules shall report on all Access transactions, Status transactions and Alarm transactions.

## Expansion Options

The “ACS” system shall provide simple system expansion options for expansion of existing hardware, software and the addition of additional sites.

## Integration

The “ACS” shall provide integration options for integration with the following third-party systems:

- Intrusion Alarm systems

- Fire alarms

- Elevators

- Human Resources Databases

- Time and Attendance Systems

- ERP, SCM and CRM Systems

- Student Enrolment Systems

- Digital and Network Video Recording Systems

## Remote Administration

It shall be possible to administer the “ACS” sites remotely by utilizing the following technologies:

- Dial-in via GPRS modem

- Ethernet

## Details

The “ACS” shall support the use of Zones and Locations to group similar functioning access points into user configurable groups.

## Zones

A zone is defined as the combination of multiple locations that allow access to and from an area.

Zones shall support the following features and functionality:

- Anti-Passback

- Embedded zones (zones within zones)

- Inter-leading zones

- Tag counting

The “ACS” shall support inter-zone communications to facilitate the transfer of transaction related data across single or multiple zones.

## Locations

A location is a single point of access to a zone and usually consists of a door with one or more readers.  Locations shall support the following hardware:

- “ACS” proprietary 125Khz antenna readers

- “ACS” proprietary 125Khz Remote reader

- Mifare 13.56Mhz readers

- RF reader

- Wiegand 125khz readers

- Barcode reader

- Mag-stripe reader

- Fingerprint Biometric readers

- Miwa locks

- Sensors – All, or a combination of the following:

- Door Status sensors

- Alarm Input sensors

- Inhibit Scanner sensors

- Emergency Mode sensors

- System lockdown sensors

Additionally, locations shall be graphically represented in the “ACS” software.

#### Tags

Tags are passive electronic devices containing a unique code.  A tag code is transmitted when it is within range of a suitable reader.  The “ACS” must support the following tag types in addition to Fingerprint Biometrics:

- 125KHz Slim and Omega tags (ISO standard Manchester encoded)

- 125KHz WriTag 128 bit

- 125KHz WriTag 2048 bit

- 13.56Mhz Mifare

- HiD

- RF 433MHz

- Infrared

#### Tag Holders

The “ACS” shall allow Tag Holders to have more than one Tag. Additionally, it shall be possible to configure different access rights on different tags.

#### Tag Modes

The “ACS” shall support the following reader modes across all locations, or in multiple combinations:

- Biometric Only

- Combination of Biometric and Tag based areas on one system

- Tag only

- Tag + PIN

- Tag + PIN + Reason Code

- Tag + Reason Code

- PIN access only

- Door Entry Code (general, single, low security code)

- Supervisor Unlock

- Locked

- Unlocked

- Dual tag requirement

- Specified Allowed tag transaction recording

- Paraplegic special entry

- APB override

- Blacklist tag

- Suspend tag

- Date-selectable auto validate and delete

#### Hardware

The “ACS” shall consist of a combination of physical components, grouped under one of the following terms:

- System Controllers

- Door Controllers

- Door Readers ( card based)

- Fingerprint Biometric readers

- Input Monitoring devices

- Output Relay devices

### Design considerations

Selected hardware must exhibit the following:

- Tamper proof construction

- If a unit is tampered with, it must generate an alarm

- In-the-field firmware upgrade

- Standards

- CE

- FCC

- RoHS

- SABS

- Pd – Lead Free

### Exposed Hardware

The “ACS” hardware shall include robust, weather resistant, vandal proof hardware. The hardware be housed in either ABS plastic housings, or metal alloy housings. The “ACS” readers shall be resistant to the following:

- Harsh weather

- Harsh environment

- Physical abuse by people

In this case, it is essential that exposed hardware be physically resistant to harsh and abusive conditions.  It must conform to at least IP53 standards, and have the IP66 option available

.

### System Controllers

The System Controllers shall be intelligent hardware devices with a full onboard database of tags and access data. The System Controllers shall operate in a truly standalone mode when there is no network connection available to the “ACS” database engine module. The System Controllers shall not have any reduced functionality when the “ACS” database engine is offline.

Each system controller shall be capable of storing up to 300 000 tags, and shall be capable of buffering up to 1 million transactions should the connection to the “ACS” polling module be lost.

The “ACS” shall support the following connectivity options between System Controllers:

RS485 – with connectivity speeds of 38400 Baud

Ethernet connectivity – with support for up to 100Mbps connectivity speeds

The “ACS” polling module shall provide an AUTODETECT function that shall poll the RS485 bus, or the LAN/WAN for any “ACS” controllers. The “ACS” controllers shall respond back with their respective factory assigned addresses which shall be automatically inserted into the “ACS” database. The “ACS” system controllers logically addresses shall automatically be assigned to the devices without any user intervention.

The “ACS” System Controller shall support up to 64 physical devices connected to its RS485 terminal communications bus.

### Door Controllers

A Door controller is a hardware device that is used to interface readers, door locks, and similar hardware with a system controller.

The “ACS” door controllers shall include the following types:

Proprietary door controllers for connection of proprietary “ACS” readers.

3rd Party door controllers for connection of 3rd Party door readers, Multi Discipline Readers and Biometric devices

RS485 -Intelligent door controllers that shall store the most recent 1000 allowed tags in its database to allow entry in the case of a communications failure with the system controller and operate in truly stand alone mode.

- Ethernet connectivity with support for up to 100Mbps connectivity of speeds.

- Intelligent TCP/IP door controllers that shall store the most recent 10,000 allowed tags in its database to allow entry in the case of a communications failure with the system controller and operate in truly stand alone mode.

Door Controllers shall have the following or a combination of the following components built in to facilitate the opening of doors and the monitoring of doors:

- Dry Contact Relays

- Digital inputs

- Antenna Ports for connection to proprietary “ACS” readers

- Communications port for connection to 3rd Party readers.

- Readers – Card Based

A reader is a hardware device that detects the unique code embedded in a tag or remote transmitter.

The “ACS” readers shall be of the following type:

- ABS Plastic

- Metal Alloy

- ABS Plastic with Keypad

- Metal Alloy with Keypad

- RF Receivers

- Stainless Steel with ABS Plastic

- Stainless Steel with ABS Plastic plus Keypad

All readers with the exception of the RF receiver shall have the following or a combination of the following components:

- Software configurable buzzer

- Software configurable Bi-colour LED

The “ACS” shall support the following Reader technologies:

- “ACS” proprietary 125Khz antenna readers

- “ACS” proprietary 125Khz Remote reader

- Mifare 13.56Mhz readers

- RF reader

- Wiegand 125khz readers

- Barcode reader

- Mag-stripe reader

- Finger Biometric Reader

- Communications

Communications between the “ACS” Server and the “ACS” system components shall have the following architecture:

- “ACS” Server to System Controller shall support either RS485, TCP/IP or UDP Multicast protocols.

- “ACS” Controllers to “ACS” terminals shall be RS485

- “ACS” Door Controllers shall support a variety of protocols including, but not limited to:

- Vendor Proprietary

- Wiegand

Communications busses shall be configurable via a star or daisy chain topology.

- Third party

The “ACS” shall provide support the following third party hardware:

- Industry Standard Fingerprint biometric readers

- Miwa lock

- Wiegand reader – 26, 44, 37bit

- Mifare reader

- Mag-stripe reader

- HID readers

#### Software

- General

The “ACS” software shall meet the following general criteria:

- Fully featured client-server architecture

- Written in Java for platform independence so it can run on non Microsoft operating systems such as Linux

- Modular design comprising the following key applications:

- Polling module

- Configuration module

- Graphic display module

- Multivendor Database Support

- Context-sensitive Help

- Modular design comprising the following support applications and utilities:

- Alarms Modules

- Employee enrolment module

- Transaction viewer with photo ID popup

- Visitor enrolment module

- Database archive site

- CSV import of tag holder information

- Translation utility

- Ethernet device Discovery utility

- General System Diagnostic modules

- Architecture

Each software module shall be able to run on individual client workstations if required.  Conversely, all software modules shall be able to co-exist on the same workstation without overloading the workstations resources.

- GUI

All “ACS” software modules shall have a graphical user interface (GUI).  The configuration GUI shall be in an easy to use Tree format displaying “ACS” functions in separate nodes.

- Translation

The Access software module shall offer a site to translate the text labels and menu items on the GUI.  The translation feature must consist of a utility that enables a user to do the following:

- Select a Locale – country

- Select a language and replace the default words with local words

- Apply the language settings via a menu command

#### Features and Functions

- General Features

The “ACS” software shall support the following features:

Holidays

Password protection on each Site

Password protection on every application and utility

Reports accessible in a web based format

Translatable to accommodate multiple languages

Time zone offset and daylight savings

Multiple time zones support

Application Help

Tag holder Archive Site

Bulk Tag holder Adding

Systems Analysis utility

Reason Code Editor utility

System Event Editor utility

Card Design utility

- General Functions

The software must be suitable for users to configure, monitor, and administrate all aspects of the “ACS” including the following:

Sites

Hardware

Tags and tag holders

Access patterns

- Backup

The software must provide for scheduled backup of data, to specific local or network directories, at specific times

- Operator Security

The “ACS” software shall include an Operator Security module that will enable the System Administrator to define operator groups for users who will operate the various modules. The Operator Security module shall facilitate the creation of Users and Passwords, and  user Groups. The System Administrator shall be able to set up Application security as well as granular security settings within each application. The Operator Security module shall facilitate the assignment of Tag holder Access groups to selected Operator groups.

#### Database

The “ACS” shall support the following database types:

- Microsoft SQL Server 2000 or later

- Firebird SQL database

- General

The database shall support a minimum of 256 Sites

There shall be no limit to the number of Tags or Tag Holders records stored in each individual Site

The database must support connection via JDBC data source

- All databases must have the following:

Full SQL compliancy

Support for multiple connections

A manual SQL querying site

Load balancing capabilities

Password protection

- Administration

Multiple users shall be able to administrate the database

Administrators shall be able to administrate the database industry standard DBMS software

- Installation

The must be provision for the database to reside on the Host PC, or on a dedicated server connected to the network.

#### Polling Module

- “ACS” database Engine

An “ACS” database engine is required to send and receive transactions to and from controllers.  This action must happen without affecting normal operation.  The “ACS” database engine module shall be capable of performing the following operations:

Auto-detecting hardware on a communication bus, and assign Logical addresses intelligently so as to avoid duplicate addresses

Comparing and validating hardware on the communication bus with hardware records in the database

Verifying hardware firmware versions

Displaying real-time transactions on demand

Scheduled back-ups with:

- A user-definable number of back-up files

- A user-definable back-up file path

In the event that the Database Server fails, the “ACS” database engine shall automatically start creating a backup of transaction logs. When communications to the Server has been re-established, the “ACS” database engine must then transfer the transaction logs to the database.

Indicating when hardware goes offline and generating an alert for this event

The “ACS” database engine shall be able to connect to the database over a networked solution separating the database server from the “ACS” software.

The “ACS” database engine shall be able to connect to the Hardware via RS232, USB or UDP.

The “ACS” database engine shall incorporate a web server that allows anyone with the correct access permissions to view transaction history of any Tagholder; this web service is not dependant on the software to be polling the hardware. The System Administrator shall have the option to allow security on the web server or allow open permissions.

The “ACS” database engine shall have an Interface to view what messages are outstanding for each controller and have the option to clear the messages.

The “ACS” database engine shall have a feature for use when using Ethernet type controllers to import their settings into the database.

The “ACS” database engine shall have an upload feature that prepares the upload data in a queue and then provides an upload to each controller.

The “ACS” database engine shall not cause any downtime of controllers should an upload be performed.

The “ACS” database engine shall provide a clear output message to the System Administrator should the upload process fail at any point.

- Advanced Options

The Database engine module shall support the following advanced configuration options:

Ability to set times and timeouts for the following:

- Controller Timeout

- Controller slow poll drop time

- Challenge Timeout

- AutoID Time

- Terminal bus additional timeout

- Controller bus additional timeout

- Uploader database connection reset time

- Uploader cycle delay

- Uploader inter table delay

- Uploader daily start time

- Uploader daily end time

- Poller inter poll delay

- Poller daily start time

- Poller daily end time

Host Interface fast polling

Terminal Bus fast polling

When using the controllers in broadcast mode set the option to transmit the broadcast twice

In the event that a controller goes offline, have the ability to relax APB until the Controller comes back online

Append carriage return to fast polling

Reset of advanced options to factory default

- Polling Module Properties

The Polling module must enable the following properties configurable:

Database type

Database driver

Database URL

Encoding key

Database encoding

Logging mode with the following options:

- No Logging

- Log outgoing messages

- Log all messages

- Log all messages longer than threshold

- Log incoming messages

- Log incoming messages longer than threshold

Auto start on startup with an auto start delay

Web Server on start with an inactivity delay

Full upload on first pass

Redirect to file

Delete expired tags

Validation on start

Set UDP Comms

Set Administrator password

Set Web Server username and password

Set Site SLA

#### Configuration Module

A configuration module shall be required to set-up a Site for access control by configuring access hardware.  System components shall be graphically represented by a hierarchical tree diagram in a left-hand pane of the window.  On selecting each component, its corresponding settings shall be displayed in the main application window pane.

The configuration module shall reference a user-configurable text-based properties file containing the following information:

Database file paths

Localization Encoding

Name of default Site

Communication Type

The properties file shall enable the System Administrator to customize preferences for using the various modules by changing settings in the file.

- Configuration Tree

The configuration tree shall contain the following nodes:

System— Display a summary of all sites’ logical Addressing, site name, site ID, and site groupword

Sites—must display and enable editing of the following information:

- Site number

- Site name

- Enforce zone routing

- Shared site option

- Daylight saving time offset in seconds

- Daylight savings time: start date and start time

- Daylight savings time: end date and end time

- There shall be an option to enable the Any Tag feature

- There shall be an option to set a Site mask for increased security

- The System Administrator shall be able to set the TCP/IP Port connectivity  numbers for the different utility modules namely:

- Transaction viewer

- Alarm

- Messaging

- Host Validation

- Door Status

Hosts—shall display host number, host name, and IP address.  Each host must drill down to display the following:

- Controller

- Zone

- Location

- Terminal

Access Time patterns—The ATP node shall enable adding of access time patterns, and editing of the following parameters for each time pattern:

- Time pattern name

- Start time

- Duration

- Days of the week

Areas— Clicking on the Areas node shall display a tree diagram of all controllers with their relevant doors and terminals, and the option to add or edit new Areas.

Tag holder access groups – clicking on the Tag holders Access groups node shall open the Tag holder Access Groups utility that shall allow the System Administrator to add up to ten thousand Access definitions by linking together Access Time Patterns and Areas

Tag holders – clicking on the tag holders node shall display all information pertaining to tag holders including:

- Personal Details – Name, surname, Notes etc.

- Custom Field Data

- Information on up to eight TAGS

Holidays

Device time patterns

Time triggered actions

Actions – It shall be possible to add or edit system actions from the actions node

Inputs – It shall be possible to alter the functionality of all defined system inputs by clicking on the Inputs node

Outputs – it shall be possible to edit the default state of all system outputs for the system by clicking on the outputs node.

Common Zones

Messages

- Host Components

Controller

When a specific System Controller node is selected, the “ACS” software shall display the Controller name, Controller parameters and have an option to enable or disable the controller.  There shall be a site to enable supported tag types and set the terminal port baud rate as part of the controller parameters

For Ethernet based controllers, there shall be an option to enter in an IP Address and Port numbers for both hardware and PC port.

There shall be a separate action tab that enables a user to add, delete, and configure preset controller actions

Zone

The zone screen shall display and enable editing of the following information and parameters:

- Zone name

- APB mode – Strict, relaxed or none

- Supervisor group for the zone

- Fully nested within zone selection

- Part of common zone selection

- Relaxed exit conditions for the zone option (time override for tags on site)

- APB lockout time in minutes

- Limit tags inside selected zone – the “ACS” shall allow limits to specific numbers of tags in each individual zone.

Location

The location screen shall display and enable editing of the following information and parameters:

- Location name

- Location type

- Interleading to zone selection

- Enforce interleading zone routing option

- Multiple tag access for one or two tags

Terminal

When a specific terminal node is selected, the “ACS” software shall display and enable the editing of the following information and parameters on a Terminal tab:

- Terminal name

- Terminal enabled option

- Position: Entry or Exit

- Disable terminal

- Must have a separate button to enable different parameters on the terminal, namely:

- Change default buzzer Volume

- Change the Same tag Timeout

- Toggle between Host validation and Controller validation

- Set the frequency of random search

- Set the Time pattern for the enabling/disabling the random search feature

A terminal mode tab shall enable the user to set the following configuration options:

- Default terminal mode with the option of including a report

- Device time pattern with the option of including a report

An Input tab shall enable the user to define and configure up to 16 digital inputs per terminal each with the following information:

- Input port number

- Input name

- Input function

Each defined input shall have an option to enable time patterns and set default input parameters to monitor open contact, closed contact or change of contact.

- Time Patterns

Time patterns shall be divided into 2 separate instances, Access Time Patterns and Device Time pattern. The “ACS” must support up to 128 Access time patterns, and up to 250 Device time patterns.

Device Time Patterns must relate to all Hardware, Access Time Patterns must relate to Groups and Tagholders. Both Access Time Patterns and Device Time Patterns shall allow the System Administrator to define the following options :

Time pattern name

Start time

Duration

Days of the week

Holidays

- Tagholder Access Groups

The “ACS” shall support up to 10 000 Access groups, each Access Group must support up to 10 access Descriptions. There shall be 2 Tabs to Separate the Tagholders Access Groups into Employees and Visitors. Tagholder  access groups shall offer the following configuration options:

Supervisor Unlock

Special Actions

Start and Expiry dates per group

- Tag Holders

The “ACS” must support the following:

Displays detailed Tag Holder information including passport-style photograph

Multiple tags per Tag Holder

Tag Holder screen has search site using first name, last name, address, company, department, or tag number

Suspension of Tags

Batch mode to load tags

Batch mode to print tags

Supports Impro Card printing

Unlimited Templates

Dual sided printing

Linked to database tables

Image import - landscape or portrait

- Holidays

The “ACS” shall support up to 32 predefined Holidays.

- IP Mapping

In the event that the Customer chooses Ethernet enabled Controllers an IP mapping section must appear that enables the Operator to view all IP addresses of controllers.

- Configuration Site

Users shall be able to customize their preferences for the access module by changing settings in a properties file.

The following configuration and set-up options shall be available via a menu:

Display properties for the following components must be configurable by selecting a swatch, or HSB or RGB values:

- Tree background

- Non selectable node text

- Non selectable node background

System event editor

- Enter custom event descriptions for specified events

- Choose whether event type is normal, alarm, or special alarm

Reason codes

- Enter or modify up to 100 descriptions for reason codes

Change fixed address

- Select a controller and change its fixed address to a new value

System user security set up

- Add or delete system users and specify user rights within each application

Event log—displays a list of the following events with the option to save values to a log file:

- Date

- Time

- User

- Event

- Description

- Detail

- Status

- Site

Camera Setup—used to integrate CCTV systems

Card designer – The card designer allows the “ACS” administrator to design multiple templates for printing Tagholder cards. The card designer shall provide the following functions:

- Placement of Database fields on the card template.

- Placement of predefined graphics on the card template.

- Placement of Custom Text on the card template.

- Placement of Circles or lines on the card template.

- Design of double sided cards

- Definition of Print medium – either to Card or to Label

Batch printing of Cards

General Configuration module properties

Database Maintenance

Batch Enrolment of Tagholders

Move tagholders between Sites

Force upload of Hardware or Tagholder data to controllers

- Reports

At Minimum, the Reports Feature shall include the following:

Access

- The Message Board Report shows the latest in and out transaction for each person.

- Last Access Report Shows where the employee is now. Must be filtered by Name, Door and Date.

- Employee Transaction Report displays a detailed report on all transactions made by employees. Must be filtered by Site, Date and Time, Person, Tag Code, Department, Event and Vicinity.

- Transaction Report displays all tagholders transactions on a specific date. Must be filtered by Name, Door and Date.

- Audit Trail Report displays all the audit transactions of what the system administrator has done. Must be filtered by Date and Type.

- First Access Report displays all tagholders First Access transaction for a specific day. Must be filtered by Name, Door and Date.

- Last Access for day displays all tagholders Last Access transaction for a specific day. Must be filtered by Name, Door and Date.

- Visitor Transaction Report displays a detailed report on all transactions made by visitors. Must be filtered by Site, Date and Time, Person, Tag Code, Department, Event and Vicinity.

- Reason Code Report displays a detailed report on all reason code transactions made by employees. Must be filtered by Site, Date and Time.

- Event Transaction report this report shows which events where triggered by an input.

Person

- Person Report displays a report of transactions for individual employees. Must be filtered by Employee, Start and End Dates.

- Zone Occupancy Report displays tagholders that are IN a specific zone.

- Absenteeism Report displays a list of employees that were absent on specific days.

- Access Pattern Report displays individual employees Time IN, Time OUT, Total Hours Worked (Last Out - Last in), Average Time In, Average Time Out and Average Hours Worked.

- Hours Worked in APB Zones Report displays an employee’s IN and OUT transactions of all Strict APB Zones. Calculates the hours worked using those IN and OUT transactions. Must be filtered by Employee, Zone, Start and End Dates.

- Person Detailed Access Report displays all tagholders who have access to a location, zone and controller.

- Person Details Report displays a detailed report for individual tagholders. Must be filtered by Person, Start and End Dates.

- Zone Occupancy Report displays tagholders that are IN a specific common zone.

- Department Report displays a report of transactions for employees in a Department. Must be filtered by Department, Site, Start and End Dates.

- Department Access pattern and Time Report displays a summarized daily hours worked and total hours worked report on all tagholders and is grouped by department. Must be filtered by Person, Department, Company, Start and End Dates.

- Department Hours Worked in APB Zones Report displays employees FIRST IN and FIRST OUT transactions. Calculates the hours worked using IN and OUT clockings of each day. Must be filtered by Employee, Department, Employer, Zone, Start and End Dates.

- Holiday Report displays the holidays in Table or Calendar format.

System

- Status Report displays all the status transactions from the controllers and terminals on a specific date i.e. Terminal timeouts, Tables corrupt and Request to Enter/Exit. Must be filtered by Date and Time.

- Door Access Report displays how frequently each door has been accessed. Must be filtered by Date.

- Alarm Report displays all alarms that have been generated by the system. Must be filtered by Date and Time.

Configuration

- Area Report displays all terminals within each area of a site.

- Access Report displays all locations that a tagholder has access to. Must be filtered by Site, Person, Tag Code, Department and Vicinity.

- Terminal Action Report. Shows all terminals and their available actions

Tagholders

- Employees Report displays all employees that have valid tags/fingerprints in the system. Must be filtered by Site and Department.

- Employees without tags Report displays all employees that don’t have valid tags in the system. Must be filtered by Site and Department.

- Employees tags without access Report displays all employees that have valid tags in the system, but no Tag Holder Access group assigned to them. Must be filtered by Site and Department.

- Tags Not Used Report displays tags that have not been used since a specific date.

- Tagholder Configuration displays detailed information on Tag Holder Access Groups.

- Visitors Report displays all visitors that have valid tags in the system. Must be filtered by Site and Department.

- Visitors without tags Report displays all visitors that don’t have valid tags in the system. Must be filtered by Site and Department.

- Visitors tags without access Report displays all visitors that have valid tags in the system, but no Tag Holder Access group assigned to them. Must be filtered by Site and Department.

- Tag Expiry Report displays tags that have expired and tags that will expire. Must be filtered by Start and End Dates.

- Tagholder Access Group Configuration Report displays all areas, zones and locations within a tagholder access group. Grouped by tagholder access groups.

Custom Reports

- The “ACS” software shall provide the option to the System Administrator to write Custom Reports that meet additional reporting requirements. This feature shall include a set of Controls that allows Scripts to be run on the Database and Produce results in a web based Format and the resulting reports shall be exportable to a CSV file.

Select Database

- In the Event that the database as been archived this tab must be able to browse to the Archived database to view Archived Transactions.

- Operator Security

The “ACS” must provide configurable security options to limit system users’ activity within it.  Such operator security must be configurable on a per user group basis.  Each password protected application or utility must have the options to do the following:

Provide a user group with one of the following:

- Full access—user is granted full access to everything in the application

- Denied access—user is denied access to everything in the application

- Customized access—user can be configured to access designated features only

Grant or deny access to the following elements and specific items within them:

- Main menu

- Tree Diagram

- Dialog screens

- Popup menus

- Toolbars

The operator security function must contain presets to allocate default security permissions to users.  A user must be able to create new presets by using an existing preset as a template.

#### Biometric Module

- The “ACS” shall have a fully integrated Biometric module that shall provide Ethernet communications to Biometric devices connected to the corporate LAN/WAN. The Biometric module shall enable the user to AUTODETECT all Biometric devices on the LAN/WAN and automatically update the “ACS” database with the Biometric Devices MAC address and related information.

- The “ACS” Biometric module shall be an online module that scans the “ACS” database for any new Biometric Templates and automatically upload the template to the relevant Biometric device.

- The “ACS” configuration module shall provide a site whereby each individual biometric device can be associated with any specific door in the access control system. This shall provide the means by which distributed templates are sent only to the relevant biometric devices.

- The Biometric Device shall physically connect to an “ACS” 3rd party interface board which shall in turn connect via RS485 to the “ACS” controllers.

#### Graphical Integration Module

A Graphical Integration module is required to graphically represent the “ACS” in an easy to use format. This shall be accomplished by the use of a combination Graphics and Text based “ACS” transactions. The Graphical Integration module shall display all the “ACS” hardware, as well as 3rd party systems hardware used in the implementation of the total “ACS”. The 3rd party hardware shall include, but not be limited to the following:

- DVR, NVR or IP Cameras connected to integrated DVR/NVR systems.

- Fire zone icons for each zone configured on the Ziton ZP3 or ZP5 panels

- Alarm zone icons for each zone configured on the Caddx NX-8E Alarm panels

The Camera Icons shall allow the operator the following functionality via the Graphical integration module:

- View Live feed from multiple cameras

- Trigger snapshot storage

- Trigger recording storage

- View Playback of individual or multiple cameras

- View alarm footage

The Fire Zone icons shall allow the operator to initiate an Emergency Unlock sequence

The Alarm Zone icons shall allow the operator to arm and disarm select panels from the software user interface

The 3rd Party hardware shall be monitored via a series of “ACS” Integration Modules. The “ACS” integration modules shall include, but nor be limited to the following:

- A CCTV integration server or integration effective through the Impro Virtual I/O module that shall support, but not be limited to the following CCTV systems:

Milestone

Bosch

Avigilon

GeoVision

Samsung

iNet/Mirasys

The Integration shall provide the following base functions:

- An Integration module shall be used to set up each CCTV system with its relevant settings.

- An integration Wizard shall be used to create user defined CCTV system actions that each CCTV system shall perform upon initiation by the Integration server. These User defined actions shall include, but not be limited to the following:

- Snapshot storage

Recording Storage

Email to user

Initiate presets on PTZ cameras

- An Integration wizard shall be used to link the user defined CCTV system actions with “ACS” system events. This shall enable the recording of CCTV footage for any “ACS” system event that is generated. The recording shall occur on a single event, or a combination of events based on the following selection criteria:

“ACS” Event

“ACS” tagholder

“ACS” Zone

“ACS” location

“ACS” reader

“ACS” Tag used

- A Ziton Integration Server that shall interrogate the ZP3 and ZP5 Fire panels for all panel configuration and automatically populate the “ACS” database with the relevant data. The Fire Zones shall be represented on the Graphical integration module x by Zone Icons.

- A Caddx Integration Server that shall interrogate the NX-8E panels for all panel configuration and automatically populate the “ACS” database with the relevant data. The alarm Zones shall be represented on the Graphical integration module x by Zone Icons.

The Graphical Integration module shall be used to graphically display the following standard “ACS” information via a plan-view schematic:

- A Base Map of the “ACS” installation site

- Buildings

- Building floors

- Access control hardware

- Configured Alarm inputs

- User Configured relays

- Events

Transactions

Alarms

Messages

Door Status

Upon selecting an “ACS” hardware device and right-clicking it, there shall be menu items facilitate the following:

- Open doors

- Trigger locked mode

- Trigger emergency mode

- Monitor door

The Graphical Integration module shall allow the operator to perform the following functions via the module menu

- Translate the software

- Define alarm response criteria by the following of a combination of the following:

Acknowledge by tag

Acknowledge by password

Acknowledge by entering an operator response

- Search for tag holder via the following fields:

First name

Last name

Department

### Displayed Events

Transactions

Transaction shall be displayed on a tab that includes the following fields:

Type

Time

Event

Terminal

Name

Tag Number

Alarms

Alarms shall be displayed on a tab that includes the following fields:

Status

Time

Event

Zone

Location

Terminal

Input name

Acknowledged by

Protocol Messages

Messages must be displayed on a tab that includes the following fields:

Time

Message

Result

Door Status

Door Status must be displayed on a tab that includes the following fields:

Terminal

Zone

Location

Status Duration

### System Diagnostic modules

The “ACS” system software shall provide a hardware diagnostic tool that shall provide the following functionality:

System Tools

  - System PING – a report of all currently connected “ACS” devices including RS485 devices or Ethernet devices.

  - Communications test to measure the responsiveness of all “ACS” devices.

Firmware Upgrade Tools for upgrading the “ACS” hardware in the field.

Misperimeteraneous tools – Set logical address, Reset memory and set communications port.

SMS module on the EC” Controller to facilitate pre- emptive support and to send or receive event driven messages/instructions.

### Fingerprint readers

The readers shall be installed in the locations as indicated on the associated drawings.

A power supply unit shall be installed to cover the equipment power requirements of every door, viz. each door must be equipped with a separate in-and-out card and/or finger print readers. The contractor shall ensure that the power supply has a continuous rating and is adequately rated for the duty. Each power supply shall be equipped and fitted with a local battery back-up site. The power supplies shall be installed above the ceiling void. The power supply unit/s shall be fed from a 230 V mains plug.

The power shall be provided by the electrical contractor, in the position as indicated on the associated drawings.

### Electromagnetic locks

The doors that will be controlled by the access control system shall be fitted with electromagnetic locks as indicated on the drawings.

The contractor shall be responsible for providing all the required fixing materials, rackets, coordination etc. to mount the locks aesthetically and securely on the secure side of the door/s. The contractor shall obtain the engineer's approval in writing for mounting detail and arrangement/s before installation commences. No claims in this regard shall be considered after installation if approval if the Engineer’s approval has not been obtained in accordance with the aforementioned proviso. The tenderer shall allow for brackets in this tender. The contractor shall ensure that mounting arrangement proposed and used shall not lessen the overall magnetic sheer or hold strength capability of the electro-magnet specified above.

In this instance, the integral door monitor feature within the electromagnetic lock shall not be used.

The new magnetic lock shall have a holding force of at least 300kg.

### Door closers

All the doors that are controlled by the access control system shall be fitted with automatic door closers. The contractor shall be responsible for ensuring that the automatic door closer units close and latch the doors closed without excessive force, wear and tear on the door hinges and excessive door frame warping.

### Door position switches

The contractor shall supply and install recessed magnetic switches in the positions indicated on the associated drawings as described below.

The open and close condition of every door that is controlled by the access control system shall be monitored by means of a flush mounted magnetic type micro switch. The magnetic switch shall be a high security bias balanced magnetic read switch with an operating and release distance of 12mm and 15mm respectively. These switches will be installed on top of the doors. The contractor shall be responsible for locating and installing the door switches so that they are able to resist defeat by means of an external magnet. The contractor shall demonstrate and validate this capability to the satisfaction of the Engineer.

### Green break glasses

Green break glass units, with back boxes, shall be installed on the secure side of some doors that are controlled by the access control system. The break glass unit shall be wired to release the power between the fingerprint readers and electromagnetic locks in the event that it is activated. This operational functionality shall be demonstrated and validate through simulation to the satisfaction of the Engineer. The contractor shall note that the break glass unit shall not be wired to the fingerprint readers as a pushbutton release input. The new break glass unit/s shall have a transparent hinged lid with a seal. The units must be able to be reset.

## INTRUDER ALARM DETECTION SYSTEM

- The control panel shall be an 4-partition panel burglary that supports up to 4 expandable to 40 zones using basic hardwired and wireless zones.

- The system shall be capable of interfacing with an long range radio (LRR) unit

- Intrusion Detection System components shall be connected using the following Cables:

- Keypads using four conductors, non-shielded cable:

- General Purpose applications

- Riser applications use

- Plenum applications use

- Zone Expanders Modules shall connect to a data bus using two-conductor non-shielded cable:

- General Purpose applications use

- Riser applications use

- Plenum applications use

- Direct burial applications use

- Unpowered detection devices connect to zone inputs using two-conductor non-shielded cable:

- General Purpose applications use

- Riser applications use

- Plenum applications use

- Powered detection devices connect to zone inputs using four-conductor non-shielded cable:

- General Purpose applications use

- Riser applications use

- Plenum applications use

- Direct burial applications use

- The Siren output shall use two-conductor non-shielded cable:

- General Purpose applications use

- Riser applications use

- Plenum applications use

- Power connections for control panels shall be made using two-conductor non-shielded cable:

- General Purpose applications use

- Riser applications use

- Plenum applications use

- Ground connections to control panels shall be made using solid insulated copper ground wire:

- General Purpose applications

- Basic Hardwired Zones: Control shall provide 8 hardwire zones with the following characteristics:

- EOLR supervision shall support N.O. or N.C. sensors

- Zones/Points shall be individually assignable to any partition.

- Optional Expansion Zones:

- Polling Loop Expansion: Control shall support up to 32 additional hardwire zones using a built-in two-wire polling (multiplex) loop interface. The polling loop shall provide power and data to remote point modules, and constantly monitor the status of all zones on the loop. The polling loop zones shall have the following characteristics:

- Individually assignable to one of 4 partitions.

- Supervised by the control panel.

- Wireless Expansion Zone: Control shall support up to 32 wireless zones using an RF receiver (fewer if using hardwire and/or polling loop zones). Wireless zones shall have the following characteristics:

- Supervised by control panel for check-in signals (except certain non-supervised transmitters).

- Tamper-protection for supervised zones.

- Individually assignable to one of 4 partitions.

- Individually assignable to bell outputs and/or auxiliary relays.

- Support wireless devices listed for Commercial Burglary using the RF Receiver.

- Partitions: Control shall provide the ability to operate 4 separate areas, each functioning as if it has its own control. Partitioning features shall include:

- A Common Lobby partition (1-3), which can be programmed to perform the following functions:

- Arm automatically when the last partition that shares the common lobby is armed.

- Disarm when the first partition that shares the common lobby is disarmed.

- A Master partition (4), used strictly to assign keypads for the purpose of viewing the status of all 4 partitions at the same time (master keypads).

- Assignable by zone.

- Assignable by keypad/annunciator.

- Assignable by relay to one or all 8 partitions.

- Ability to display burglary and panic and/or trouble conditions at all other partitions’ keypads (selectable option).

- Certain system options selectable by partition, such as entry/exit delay.

- User Codes: Control shall accommodate 60 user codes, all of which can operate any or all partitions. Certain characteristics shall be assigned to each user code, as follows:

- Authority level (Master, Manager, or several other Operator levels). Each User Code (other than the installer code) shall be capable of being assigned the same or a different level of authority for each partition that it will operate.

- Opening/Closing central station reporting option.

- Specific partitions that the code can operate.

- Global arming capability (ability to arm all partitions the code has access to in one command).

- Use of an RF (button) to arm and disarm the system (RF key must first be enrolled into the system).

- Peripheral Devices: Control shall support up to 28 devices, which can be any combination of keypads, RF receivers, relay modules, and interactive phone module. Peripheral devices shall have the following characteristics:

- Each device set to an individual address according to the device's instructions.

- Each device enabled in system programming.

- Keypad: Control shall accommodate up to 12 keypads The keypads shall be capable of the following:

- Performing all system arming functions.

- Being assigned to any partition.

- Providing four programmable single-button function keys, which can be used for:

- Panic Functions: activated by wired and wireless keypads; reported separately by partition.

- Keypad Macros: 32 keypad macro commands per system (each macro is a series of keypad commands). Assignable to the A, B, C and D keys by partition.

- Optional Output Relays: A total of 6-38 relay outputs shall be accommodated using relay modules. Each relay module shall provide 4 Form C (normally open and normally closed) relays for general-purpose use. The relays shall be capable of being:

- Programmed to activate in response to system events.

- Programmed to activate using time intervals.

- Activated manually.

- Assigned an alpha descriptor.

- Optional Interactive Phone Module: The control shall support the IP Modules, which permit access to the security system in order to perform the following functions:

- Obtain system status information.

- Arm and disarm the security system.

- Control relays.

- Battery saving feature.

- Wireless Equipment: Control shall be compatible with Wireless Security equipment including:

- Commercial Wireless Receiver:

- The receiver shall be capable of receiving as many points as the control panel is rated for.

- Up to 1 Receivers may be used on the system.

## CCTV SYSTEM

### System - General Requirements

    - The video management software (VMV) shall be an open architecture Video Surveillance System.

    - The system shall be a digital video/audio recording and remote monitoring system with a capability of simultaneously displaying, recording, replaying, searching, and transmitting both video and audio.

    - The system shall be truly hybrid in nature, and shall be capable of supporting the following video sources:

- I.P. Video cameras (most popular brands are to be included in this) A separate list of supported I.P. cameras is to be provided.

- I.P. video encoders (3rd party).

- Video systems.

- ONVIF compliant devices.

    - The system shall use Universal Plug and Play (UPnP) and ONVIF Device discovery to discover I.P. devices and retrieve the settings from those devices.

    - The system shall be of a “client/server” nature with the following components:

- Recording Management Servers.

- Client viewing and management stations.

- On-site clients.

- Off-site clients.

- Off-site PDA/Cell phone/Tablet clients.

- Alarm Management Server.

    - The system shall be capable of running in a Windows (32 or 64 bit), or a Linux, operating system environment.

    - The software shall be capable of running in a “virtual server” environment. (For example VMWare).

    - Each recording management server shall be capable of managing multiple IP camera video streams, limited only by hardware processing capability, and available local/remote system storage.

    - The overall system shall have no limit to the number of cameras/video streams.

    - The system shall enable remote users to connect to the system via ADSL, VPN, or any other source of communication. It shall be able to perform ALL on-site capability and setup, via this remote connection.

    - The system shall have a true remote setup client, and not rely on remote desktop applications.

    - The system shall maintain user activity logs.

    - The system shall enable all sub-systems on site to be time-synchronised.

    - The system shall manage an unlimited number of Inputs and Relay outputs.

    - The system shall provide setup wizards for fast, simple addition of cameras.

    - The system shall store complete site configuration on site (or off-site) for retrieval in the event of hard drive failure. This configuration shall be easily re-instated.

    - The system shall be easily upgraded to later versions via a CD, USB key, or other means.

    - The system shall be easily expandable by the addition of I.P. camera licenses, or analogue system hardware.

    - Special features shall be pre-built into the system, and may be unlocked with a software key, enabling a qualified user to quickly activate these features as required.

## Video/Audio Streaming and Storage Management

    - The system shall manage the recording, and streaming, of both video and audio from the various sources.

    - The system shall be capable of:

- The system shall enable the user to designate a camera as “covert”. In this case, the camera should only be seen and viewed/reviewed by users with the relevant access rights.

- The system shall be capable of “trans-coding” video streams to a lower bandwidth, for off-site monitoring (subject to the availability of suitable video streams & the processing power of the video servers).

- The system shall provide a “monitor” recording feature, which enables the recording of any display monitor (VGA/HDMI) connected to any Windows device as if it were an I.P. camera. All functionality associated with a standard I.P camera shall be applied to this video stream.

- The system shall control access rights for archiving and reviewing of archived video footage.

- All archived video shall be signed with a digital signature for authenticity, and the signature shall be encrypted. The system shall be Kalagate approved.

- The system shall provide the facility to add a user selectable watermark to video being archived.

- The system shall provide the facility to add a random, system generated, or user generated, password to video being archived.

- The system shall be capable of storing video footage from the same cameras to multiple databases simultaneously. The databases may be on the same recording server, or on a network storage device.

- The system shall provide a “copy and paste” capability which will enable users to easily copy all camera settings, including information from multiple video streams, across multiple cameras.

- The system shall provide the capability to perform a scheduled backup as follows:

- Archive selected cameras.

- Archive only a selected period of recorded footage.

- Archive at a selected time of day.

- The system shall provide the capability to create Privacy Zones in a camera’s feed.

    - Privacy Zones shall be areas that are not viewable by Operators in a camera’s feed.

    - Privacy Zones must be editable/addable after camera addition.

    - These privacy zones must be present in live, review, and archived video footage.

    - The software must be capable of hiding/showing privacy zones (this capability must be dependent on user access rights).

    - Privacy zones’ presence in archived footage must be dependent on whether or not they have been hidden/shown by the user.

## Graphical User Interface (GUI)

    - The system shall provide a graphical user interface (GUI) which enables users to easily see all resources (Cameras, Audio components, databases, Inputs, Outputs, Layouts etc.) on a complete site, and shall not be limited to specific DVR’s or I.P. Network Video Servers.

    - The GUI shall be capable of being viewed over up to 4 monitors from one client software computer. The user shall be able to customise the monitors so that they can view different components (e.g. maps, cameras, integration data etc. on different monitors or on window “tabs” on the same monitor).

    - The layout of the user interface shall be customizable. System functions or features that are not activated, or to which the user does not have access shall be hidden from view – the user shall only see functions that he/she uses.

    - User access to site resources shall be access-controlled by username and password, whether local or remote viewing, restricted by the access level of the individual user.

    - The software shall enable users to create folders, and allocate resources to selected folders in the interface.

    - From the GUI, it shall be possible to open multiple sites simultaneously and display them on selected monitors on the system. This includes site maps, camera feeds and other site resources.

    - In order to ensure that there is fast access and bandwidth management for remote client connections, all site resources, maps, and other site specific parameters shall be downloaded and stored locally at the remote client’s location. If they have been modified at site they are to be re-loaded from the site to the remote client connection upon re-connection.

    - The system shall enable the user to select specific cameras to be viewed on selected monitors, or selected panels within selected monitors.

    - The system shall enable users to view and pause live cameras.

    - The system shall enable users to playback recorded footage.

    - The system shall allow specific cameras to be viewed live, and played back simultaneously, and synchronised together if requested.

    - The system shall allow multiple cameras to be played back simultaneously and synchronised together if requested.

    - The system shall provide the capability to drag-and-drop cameras from a resource panel into selected monitors, or panels on the monitor.

    - The system shall enable users to drag-and-drop cameras, from a map, into selected monitors or panels on the monitor.

    - The GUI shall allow the same camera to be viewed live on multiple monitors or panels on one monitor.

    - The system shall enable the configuration and initiation of tours of cameras on selected monitors or on panels within a selected monitor.

    - The system shall provide the capability to create and save multiple “layouts” of cameras that can then be easily selected, either manually by a user, or automatically on an event.

    - The system shall allow the configuration and initiation of tours of “layouts” (also known as a “salvo”) to selected monitors.

    - The system shall enable the user to “de-warp” video from 180 or 360 degree panoramic cameras.

    - The system shall enable the user view up to 64 cameras on a single monitor.

    - The GUI shall enable users to digitally zoom into specific camera views.

    - If a camera is configured to supply multiple streams, and both streams are designated for live viewing, then the GUI shall allow users to choose which stream to show for live viewing.

    - The GUI shall be able to optionally show VMD algorithms functioning by displaying overlays of:

- VMD triggers.

- VMD zones.

- VMD detection areas.

    - The system shall enable users to control PTZ cameras from the GUI, or from an attached keyboard/joystick controller in order to:

- Pan, Tilt and Zoom.

- Move PTZ camera faster and slower.

- Focus and Iris control.

- Set PTZ camera pre-set positions.

- Assign unique names to PTZ camera pre-set positions.

- Move to PTZ camera default positions.

    - Reviewing and Archiving Video Footage.

- The system shall enable users to easily review any camera on the system, from any client software connected to the system, either off-site or on-site.

- The GUI shall enable the synchronisation of cameras during playback.

- The GUI shall enable the user to mark start and end times of video to be archived.

- The system shall enable users to archive multiple cameras simultaneously.

- The system shall enable users to archive selected footage from one or multiple cameras to DVD, USB Memory device, local or remote Hard Drives.

- The system shall enable the user to save the archive “player” along with the video.

- The system shall enable users to pause playback of video and print, copy to a clipboard, or save an image to a select storage location.

    - The user should be able to control outputs from the GUI.

    - The user should be able to see input triggers from the GUI.

    - Map Interface.

- The system shall provide a multi-layer interactive map facility.

- The map facility shall be hierarchical with “drill-down” capability.

- The system shall enable users to drag-and-drop cameras from the map to monitors for viewing.

- The system shall enable users to trigger an event from the map by “clicking” on a map icon.

- The system shall enable remote users to automatically view the site map.

- The system shall enable remote clients to download and store the maps locally to remove the need to download the map for each connection.

- Comprehensive map setup/editing software shall provide the means to create and edit maps. This software shall include at least the following functions:

- Setup Wizard.

- Vector drawing tools.

- Image import.

- Detailed, editable properties for all objects.

- Cloning object properties to other objects.

- Create object actions.

- Layers have transparency / hide- show.

- Object and entire map rotation.

- Comments.

- Optional grid.

- Cameras with editable fields of view.

- Domes with associated, editable presets.

- Color and texture fills.

- Object ordering and list per layer.

- Editable text.

- Create map hyperlinks.

- Zooming.

- Adding cameras with drag-and-drop icons (fixed or PTZ).

- Association of icons with system cameras.

- Adding of I/O via drag-and-drop icons.

- Importing of graphics in JPG or PNG format.

- Ability to associate layers with preset PTZ positions.

- Ability to switch layers on or off in response to a system event (e.g. to indicate a door opening/closing).

- Drag site resources from a site resources list directly to the map.

.

## Events triggers and Actions

    - The system shall provide an event and action management capability with the following features.

    - Events.

- The system shall have the ability to trigger events on the following:

- Trigger from cameras/encoders on the network. This includes physical inputs or Video analytics triggers.

- Built-in motion detection.

- 3rd Party Devices (e.g. Access control, Fire Panels, Alarm Panels, Point-Of-Sale, etc.).

- Local user events (events initiated by an operator).

- Recordings initiated by a time schedule.

- The system should have an “AND” function which will prevent triggers occurring unless an event trigger AND an I/O input is present.

- The system shall enable the user to specify event specific, validity schedules.

- The system shall provide a “debounce” delay setting to limit the frequency of triggers.

    - Actions

- The system shall be able to perform one or more of the following actions upon the receipt of an event trigger:

- Perform an action either “while” an event is occurring or “when” an event occurs.

- Record video footage from one or more cameras to a selected database.

- Record pre-events from one or more cameras.

- Record synchronised video and audio.

- Switch or toggle one or more relay outputs which are provided by the system or cameras/encoders connected to the system.

- “Pulse” one or more relay outputs which are provided by the system or cameras/encoders connected to the system.

- Move one or more PTZ cameras to “preset” positions.

- Switch one or more selected cameras to one or more selected monitors connected to the system.

- Switch a camera “layout” to a selected monitor.

- Record data from a 3rd party system (e.g. Point-Of-sale, Access control, Alarm panels).

- Initiate a graphical action on a map.

- Play a pre-recorded audio clip via the local client server OR via an audio output on an I.P. camera or encoder.

- Send an email to selected recipients.

- Send an alarm to a user viewing the system via the Viewing software and Alarm Management Gateway (see Section 9). This is applicable to local or remote systems.

- On an action that is sending an alarm, or notifying a user, there shall be at least 3 user-defined levels of priority that may be allocated to the specific events.

- Upon sending a notification to an Alarm Gateway, the system shall allow the user to define video previews to be sent with the event notification.

- There shall be a user defined delay option to limit the number of alarms sent.

- Stop a previously initiated action.

- All actions shall be subject to user defined time schedules.

    - The system shall provide the ability to create “event templates” which will enable users to easily associate common actions across multiple cameras.

## Video analytics

    - The system shall be capable of utilising the on-board analytics on the I.P. camera or encoder to initiate an event with which selected actions can be associated as per paragraph 5

    - The system shall have built-in Video Motion Detection algorithms, and will be capable of performing these on video streams received.

    - The built-in motion detection shall have the following features:

    - Variable sensitivity.

    - Size masking.

      - Reject objects smaller than a specified size.

      - Reject objects larger than a specified size.

    - Multi-zone VMD areas per camera with the ability to vary sensitivity in each zone.

    - It shall be possible to employ an advanced version of the video motion detection that uses a learning algorithm to detect a noise level (e.g. slow cloud movement, slow movement of trees in wind, background traffic, and moving machine parts) and to generate a mask to eliminate these ambient movements as false triggers. The mask shall decay when repetitive ambient movement ceases, thereby minimizing false alarms, and reducing irrelevant recordings, alarms, and security responses.

    - A day/night setting capability to enable different VMD settings for day and night. Automatic day/night switching or switching at specified times are to be optional.

    - A schedule which enables/disables selected VMD triggers at certain times of day.

    - The ability to track moving objects as they move through different areas of a facility. In response to this movement, PTZ cameras shall be moved to preset positions.

    - The system shall have the capability to add analytics like people counting, “abandoned object”, “removed object”, Automatic Licence Plate Recognition (ANPR), and line crossing detection under license.

    - Motion detection trigger images are to be stored to the database, and associated with any recordings completed due to that motion detection trigger.

    - The GUI shall have the capability to show.

    - Masking areas of VMD.

    - VMD triggers.

    - VMD detection areas.

    - The VMD setup window shall enable users to view live or recorded video, for VMD setup/testing purposes.

## Integration

    - The system shall have the capability to integrate 3rd party products like Access Control, Point-Of-Sale, Alarm Panels, and other devices capable of communicating data via RS232 or Ethernet.

    - The integration capability will be dependent on the integrated device but the system shall be capable of the following features:

    - Reception of data from the 3rd party device.

    - Perform specific triggers and actions dependent on specific data received.

    - Perform triggers and actions on specific data.

    - Store the data in logical fields in a selected database.

    - Associate video data from one or more cameras with specific data events.

    - Provide the ability to “mine” the database to find selected data/transactions and the associated video data.

    - Synchronise the video and data in time using Network Time Protocol (NTP).

    - Play back video and data simultaneously and synchronously.

    - Provide easy filtering of database data for search purposes.

    - Provide “quick-search” capability via a drop-down user interface.

    - Provide a live display of data received and simultaneously view associated cameras.

    - The system shall integrate with I/O devices to control outputs and receive inputs from the I/O devices. These devices may be on a network camera, encoder (server), or on a dedicated network I/O device.

## Support, Health Monitoring and Technical Reports

    - The system shall provide a complete remote setup and maintenance client. Remote desktop applications are not acceptable.

    - The remote setup client shall have the same complete functionality of the server software.

    - The system shall keep logs and provide reporting capability of the following.

- Hard drive integrity and failures.

- Reboots.

- Cause of reboots, including:

- Software server reboots.

- Power failure reboots.

- User reboots.

- Remote user reboots.

- Time of reboot.

- Camera failures.

- Software server failures.

- System setup and configuration.

- Recording setup and configuration.

- Recording times of the system, per camera.

- System temperatures.

    - It shall be possible for users to save their reports as “templates” for easy generation of future reports.

    - It shall be possible to export reports in either text or html format.

    - It shall be possible to email reports.

    - It shall be possible to print and archive (save) reports.

    - Reports shall be in html format, with automatic generation of a table of contents, and hyperlinks to sections.

    - It shall be possible to automatically compile and email selected reports to selected recipients to a specified schedule.

    - The system shall be capable of sending alarms to a user or an Alarm Management Gateway if any of the following occurs:

- Cameras failed more than a specified number of times in a specified time period.

- Cameras were down for more than a specified percentage of time in a specified period.

- System temperature greater than system requirements.

- Fan speeds of system below requirements.

- Hard drive SMART parameters outside system required norms.

- If the number of recorded events on any particular day is less than it should be (based on an historical mean), indicating a possible technical fault.

- If an unusual shutdown sequence has occurred (e.g. a user pulls out the power lead).

- If there is digital indication that a camera lens has been spray-painted or completely covered by other means.

- If a communications medium has failed (e.g. Ethernet or Modem).

- If the reboot frequency is unusually high.

- If an automated routine base station ping of a capture station has failed.

- It shall be possible to set the system to trigger a technical alarm if an IP encoder or camera goes down.

- It shall be possible to trigger a test technical alarm from a single unit within a site of units.

- All systems shall continuously test all other systems on the site for “up-time” and if any systems do not respond, then an alarm may be sent.

    - The sending of alarms shall have filters to enable users to limit the number of alarms sent. These settings shall include:

- Send alarm each time an event occurs.

- Send alarm immediately and then every specified time period.

- Send alarm once only.

## Alarm Management Gateway

    - The alarm management server shall have a database that manages all alarms sent from one or more sites.

    - The alarms database shall be available for viewing, and for handling alarms, from multiple client desktops under password control.

    - The alarm gateway database shall be used to store unit lists, incoming alarm data, full audit trails, plus downloaded video and audio, providing for centralized control of all relevant data.

    - The database shall also feature search filters to mine the database.

    - It shall be optional to assign audio notifications to the different priority incoming alarms.

    - Where incoming alarms are unhandled in the incoming queue, the highest priority alarm in the incoming queue shall sound its audio notification every thirty seconds, until handled.

    - It shall be possible to customize the incoming alarm audio notifications.

    - Alarms shall display sequentially in separate panes: incoming (awaiting handling), current (being handled) and archived (handled).

    - An operator shall be able to respond to an alarm and automatically connect to the site from where the alarm was initiated.

    - The system shall be optionally configured so that, on connection, the operator shall see the client-customized desktop / screen configuration, alarm information, and map pertaining to that particular alarm. It shall be possible to configure the map so that an event alarm icon flashes at the appropriate point where the alarm was initiated.

    - It shall be possible to temporarily disable (block) repetitive invalid alarms for specified periods. This blocking shall be specified from the capture unit, and shall require explanatory comment by the blocking operator.

    - It shall be possible for operators to simultaneously clear multiple alarms from the incoming queue.

    - Operators shall be able to handle multiple remote alarms simultaneously - a separate interface tab shall represent each connection.

    - Where multiple operators are handling alarms, the system shall keep all operators informed as to an alarm’s status, and who is handling which alarm.

    - Even when out of the alarm-queue desktop, operators shall still see an alarm status bar indicating the number of incoming, un-handled alarms by color-coded priority.

    - Operators shall be able to add comments to Current and Archived alarms. To facilitate fast responses, default comments shall be selectable from a menu, but it shall also be possible to add custom text comments.

    - It shall be possible to modify the default comments menu with more appropriate custom comments.

    - Control room operators shall optionally use dual, triple or quad-monitor interfaces, with Alarm, Resources, Map desktops, and other software spread across the monitors.

    - The software shall enable systems to be connected using TCP/IP, over LAN/WAN on Ethernet/Token Ring or PSTN/ISDN. These connections shall be on a “mix-and-match” basis.

    - The alarm interface shall feature a clearly-visible graphical indicator of the gateway-connection status (connected or disconnected).

    - The alarm interface shall be access-controlled independent of the remainder of the software, and shall have its own user management utility.

    - The control room solution shall be capable of bi-directional audio transmission and monitoring.

    - Operator logins, and responses to incoming calls, shall be recorded by an Audit Trail facility that is protected from manipulation.

    - It shall be possible for operators to electronically escalate an alarm to a “case”, and assign people to investigate, thereby alerting and involving security management structures.

    - It shall be possible to create a case independently of an alarm.

    - The system shall establish an audit trail and timeline of case responses, enable electronic collaboration between all assigned parties, commit important personnel to the process, and ensure that the case has to be properly resolved/signed off before it can be “closed”.

    - Users to whom cases have been escalated shall receive electronic notification of case assignments.

    - A case management utility shall provide the means to manage the formal security process from the alarm interface.

    - Case managers shall be able to further escalate cases, to higher and higher levels of inspection.

    - The system shall provide detailed, customizable reports based on connections, response times, logins, and handling times.

    - It shall be possible to schedule the system to run reports automatically, and to perform automated actions with the reports, such as emailing the report to recipients.

    - The alarm management system shall monitor connections to remote units via phantom alarms (a site heartbeat) at set intervals. It will generate a trigger when a remote alarming unit fails to send its phantom alarm.

    - It shall be possible to send technical and event alarm SMS’s from the alarm management system.

    - It shall be possible to filter historical alarms using their associated recordings and metadata. Filter parameters shall include Alarms, Sessions (where multiple alarms may have been sent through on a single connection), control-room Operator (based on login information), and Cases (alarms that were escalated for further investigation).

    - From the historical alarms interface it shall be possible to double-click an entry (Alarm, Session, Operator Login, Case) for a more detailed information/action screen related to that entry, from which it shall be possible to do the following:

- View alarming site name.

- View alarming server name.

- View alarm description.

- View control-room Operator who handled an alarm or a session.

- View the name of the control-room unit through which an alarm or session was handled.

- View time of an alarm event.

- View time that an alarm event was dispatched to the control room.

- View an alarm’s arrival time at the control room.

- View time taken to handle an alarm by the control-room Operator.

- View Comments associated with alarms, sessions and cases.

- View recordings associated with an alarm.

- Archive associated alarm recordings to CD/DVD/USB.

- Connect to the historical alarming site to fetch further recordings associated with the alarm, if they still exist in the remote site’s database/s.

- View Cases associated with an alarm.

- Show the entire Session in which an alarm was handled.

- Add further Comments to historical alarms, sessions and cases.

- Escalate an historical alarm to a Case for further investigation and resolution.

- Show the entire Session in which an alarm was handled.

- Show control-room Operator logins associated with an alarm session.

- View all alarms associated with a session.

- View a control-room Operator’s login duration, start time and end time.

- View the number of Sessions handled by a control-room Operator during a Login.

- View all Sessions handled by a control-room Operator during a Login.

- View a Case description.

- View the name of the user who escalated an alarm to a Case, with the date-time.

- View the name of the user who closed a Case, with the date-time.

- View a list of Case users, with their Status relating to a Case (Active - still working on it, or Inactive – no longer working on it).

- View a Timeline of user actions relating to a Case.

- View the Status of a Case.

- View all Alarms associated with a Case.

- View all Comments associated with a Case.

## System security and Access Rights

    - The system shall have an optional technical alarm that warns the user and/or a control room if unusual system shutdowns/reboots have occurred.

    - The system shall have an optional technical alarm that warns the user and/or a control room if an image is recorded at a very low image size from any camera, as would happen with the spray-painting or otherwise blocking of camera lenses.

    - User Access shall be configurable at an Administrator-level plus thirty further levels of user access.

    - The system shall be accessed by user name and password, and all user actions shall be recorded against the user’s name in an operator audit trail. This audit trail shall be accessible, printable, and access-controllable.

    - It shall be possible to specify a limit to the user login period, after which users must login again.

    - Access for remote users shall be controllable from the local system rather than from the remote viewing system.

    - It shall be possible to restrict access on the set-up and viewing of databases, cameras, remote units, communications, operational panels, and system set-up functions.

    - It shall be possible to “hide” selected databases, and camera views, from specific levels of system user, so that the user is unaware of their existence.

    - For prosecution, and other legal purposes, recorded images shall be digitally signed with a unique identifier that is lost if an attempt is made to manipulate the image.

## Audit Logs

    - Users with appropriate access rights shall be able to view and print audit trails of operator and system activity from the graphical user interface.

    - An operator log shall provide an historical log of operator actions, across all user logon names. This Operator Log shall be able to be used for:

- Research operator responses to situations (e.g. whether operators followed correct procedures after an alarm notification).

- To track configuration-related actions (e.g. renaming, enabling, disabling, re-configuring, setting up).

- To track individuals responsible for security breaches, and

- To perform any other activity that is made possible by a detailed knowledge of user actions.

    - The operator log information shall be presented in a screen interface that provides options in sorting the information, including sorting by specific user, by all users, by operator changes to the local system, and by operator changes to remote systems.

    - A system log shall provide an historical log (list) of automated (system) actions.

## Integrated keyboard

    - The system shall feature an integrated keyboard control.

    - The keyboard joystick shall be able to function as a mouse or a dome controller, enabling operation with a VGA graphical user interface or an analogue camera display.

    - The keyboard shall feature fast key-selection of cameras, presets, VGA monitors, outputs, camera tours and screen layouts.

    - Dome camera function buttons shall be accessible to the fingers of the hand on the joystick, so that operators need not relinquish control of the joystick.

    - The keyboard LCD display shall be writable by the digital surveillance system.

    - Keyboard key LEDs shall indicate the state of keys and functions.

    - It shall be possible to adjust the joystick’s pan and tilt sensitivity.

## Failover

    - The system shall have provision for a failover server.

    - A hot-spare structure will be used to accomplish this.

    - The failover server will continually monitor recording servers.

    - System alarms will be generated if a failover slave server is down.

    - The failover server will assume full functionality of a failed slave recording server.

    - The site will continue to function as if the recording server had not failed.

    - Video will be re-inserted on the original recording server’s database on recovery.

    - A single failover server can only assume the functions of a single failed recording server.

    - Multiple failover servers will be required to assume the functions of multiple failed recording servers.

    - Failover servers will have unique IP addresses.

    - Failover servers will require camera licenses equal to, or great than, the number of cameras on the recording server that is to be failed over. Camera licenses will be equally shared across multiple failover servers.

    - Each failover server will require a failover server license with a warning in the status bar if it is unlicensed.

    - Only NVRs can be failed over. NetBSD servers, and servers with frame grabber cards, are excluded.

    - A Site master NVR will have limited failover, and will require alternate provision for 100% failover.

- With a failed-over master NVR there will be limited functionality on the site – recording will continue on the failover server, but the IP address will be different to that of the original site master NVR.

- The site will not be externally accessible on the original master IP address.

## Forensic tool

    - The system shall have provision for a forensic tool to troubleshoot and obtain the following historical site server data:

- Network camera summary – total network throughput, drop ratio, and count of camera stalls.

- Database writes - disk writing bitrate, and drops to local or network storage.

- Dropped packets – external network, internal UDP between servers, and internal video frames.

- Video streaming – sent, received, and decoded for live viewing.

- Software compressor – encoded and decoded pixel rate, and percentage of frames.

- Internal messaging – UDP packets missed and received between processes, and number of logs per minute sent.

- Video frames – missed and received between internal processes.

    - The system shall have provision for a forensic tool to troubleshoot and obtain the following historical camera-specific data:

- Network cameras – bitrate, dropped packets, cameras stalls, camera down, and number of events per camera.

- Database cameras – bitrate, bytes written to disk, camera down, and number of events per camera.

    - The system shall have provision to present the forensic data in a graphical format based on the following:

- Date and time selection.

- Time frame selection.

    - The system shall have provision whilst in the Graph Window to facilitate the following:

- Zoom in on a time period of data.

- View the data values.

- Export as a Comma Separated Values (CSV) file.

### Video Management Server / Recorder (Type 1)

- General Characteristics:

      - The IP Video Management Appliance shall manage all IP and digital video, audio, and security data transmitted across an IP network.

      - The IP Video Management Appliance shall come with a pre-installed VMS license for connecting 32 concurrent recordable cameras.

      - Software updates shall be available free of charge during the product warranty period. The software installed on the IP Video Management Appliance shall not be subject to any additional Software Maintenance Agreements (SMAs).

      - The IP Video Management Appliance shall be a pre-configured and pre-installed IP video management solution with up to 8 TB (4 x 2 TB) storage capacity.

      - The IP Video Management Appliance shall offer front-swappable SATA-II hard drives providing 8 TB of gross storage capacity.

      - The IP Video Management Appliance shall run the Video Streaming Gateway to allow third-party camera integration.

      - The IP Video Management Appliance shall allow remote viewing via the Video Security App.

      - The IP Video Management Appliance shall offer a maximum of up to 8 TB of gross capacity storage with a corresponding 7400 GB of net storage capacity.

      - The IP Video Management Appliance shall offer a bandwidth of 120 Mbit/s (read and write).

      - The IP Video Management Appliance shall offer an Intel Core i3-2120 processer.

      - The IP Video Management Appliance shall utilize Microsoft Windows Storage Server 2008 R2 (64-bit).

      - The IP Video Management Appliance shall be configurable to a RAID-1 software configuration (with reduced performance and net capacity values).

- Functions

      - The IP Video Management Appliance shall come pre-installed and pre-configured with all necessary software.

      - The IP Video Management Appliance shall enable viewing of high-quality HD video despite low or limited bandwidth by utilizing Dynamic Transcoding technology.

      - The IP Video Management Appliance shall decode and decompress the data stream to a lower bit rate stream tailored to the bandwidth of the connection.

      - The IP Video Management Appliance shall offer Disk on Module (DoM); a solid-state, non-volatile memory module that contains a backup image of all system software needed to a full system recovery.

- Management

      - The IP Video Management Appliance shall provide a user interface for system configuration and unified appliance management.

      - The IP Video Management Appliance shall come with the VMS management application pre-installed and pre-licensed.

      - The IP Video Management Appliance shall allow operators to use one central tool for configuration and operations management.

- Remote Viewing

      - The IP Video Management Appliance shall provide the VMS Client for remote viewing and archiving.

- Storage

      - The IP Video Management Appliance shall contain four (4) 3.5 in. SATA storage trays.

      - The IP Video Management Appliance shall have four a maximum of (4) HDD (2 TB 5400 RPM GP) hard drives installed.

      - The IP Video Management Appliance shall include one (1) USB DVI port, onboard graphics VGA port.

      - The IP Video Management Appliance shall include a 1x1 GbE Rj45 network port.

### Video Management Server / Recorder (Type 2)

- General Characteristics

      - The IP Video Management Appliance shall be a RAID-5 protected, all-in-one recording, viewing and management solution for network surveillance systems of up to 128 channels.

      - The IP Video Management Appliance shall come with a pre-installed VMS license for connecting 32 concurrent recordable cameras.

      - The IP Video Storage Appliance shall offer an optional camera expansion license for 8 additional concurrent recordable cameras up to a maximum of 128 cameras per appliance.

      - Software updates shall be available free of charge during the product warranty period. The software installed on the IP Video Management Appliance shall not be subject to any additional Software Maintenance Agreements (SMAs).

      - The IP Video Management Appliance shall utilize “enterprise-rated” hard drives in a fault tolerant RAID-5 configuration.

      - The IP Video Management Appliance shall be a pre-configured and pre-installed video management solution with up to 16 TB (8 x 2 TB) of gross storage capacity.

      - The IP Video Management Appliance shall offer up to 12930 GB of net capacity storage.

      - The IP Video Management Appliance shall offer a bandwidth of 200 Mbit/s.

      - The IP Video Management Appliance shall offer a dual port Gigabit Ethernet network interface, 4 GB system memory and an Intel Xeon Quad Core Processor.

      - 10.	The IP Video Management Appliance shall offer remote monitoring via a desktop application or a Web browser.

- Functions

      - The IP Video Management Appliance shall offer an energy-efficient hot-swap redundant power supply.

      - The IP Video Management Appliance shall offer hot-swap SATA-II hard drives providing up to 16 TB of gross storage capacity.

      - The IP Video Management Appliance shall come pre-installed and pre-configured with all necessary software.

      - The IP Video Management Appliance shall utilize Microsoft Windows Server 2008 R2.

      - The IP Video Management Appliance shall offer Disk on Module (DoM); a solid-state, non-volatile memory module that contains a backup image of all system software needed to a full system recovery.

- Access to Video

      - The IP Video Management Appliance shall deliver high-quality HD video despite low or limited bandwidth connections.

      - The IP Video Management Appliance shall offer Dynamic Transcoding technology that retrieves data and subsequently decodes and decompresses the data stream to a lower bit stream.

      - The IP Video Management Appliance shall instantly enhance the video detail to full HD quality when the video is paused.

- D.	Management

      - The IP Video Management Appliance shall come with the VMS management application pre-installed and pre-licensed.

      - The IP Video Management Appliance shall offer the Microsoft System Center Suite built-in.

      - The IP Video Management Appliance shall allow operators to use one central tool for configuration and operations management.

- Health Monitoring

      - The IP Video Management Appliance shall provide SNMP, Remote Desktop and HTTP monitoring support.

      - The IP Video Management Appliance shall offer high-availability hardware, embedded design, and system wide monitoring.

- Storage

      - The IP Video Management Appliance shall contain eight (8) 3.5 in. SATA storage trays.

      - The IP Video Management Appliance shall have 16 TB, 2 TB SATA/3000

(7,200 RPM, 32 MB cache, 3.5 in.) hard drives installed.

      - The IP Video Management Appliance shall offer a 2108-based SAS/SATA RAID card with 8 internal ports/low profile-PCI-E.

      - The IP Video Management Appliance shall include an AMD FirePro V3900 1 GB, low profile graphics card

      - The IP Video Management Appliance shall include a Creative Sound Blaster PCI sound card.

      - The IP Video Management Appliance shall include an Intel SSD 320 OVR, 80 GB (MLC) OS drive.

### Video Management Server / Recorder (Type 3)

- General Characteristics

      - The IP Video Management Appliance shall be a RAID-5 protected, all-in-one recording, viewing and management solution for network surveillance systems of up to 128 channels.

      - The IP Video Management Appliance shall come with a pre-installed VMS license for connecting 32 concurrent recordable cameras.

      - The IP Video Storage Appliance shall offer an optional camera expansion license for 8 additional concurrent recordable cameras up to a maximum of 128 cameras per appliance.

      - Software updates shall be available free of charge during the product warranty period. The software installed on the IP Video Management Appliance shall not be subject to any additional Software Maintenance Agreements (SMAs).

      - The IP Video Management Appliance shall utilize “enterprise-rated” hard drives in a fault tolerant RAID-5 configuration.

      - The IP Video Management Appliance shall be a pre-configured and pre-installed video management solution with up to 24 TB (8 x 3 TB) of gross storage capacity.

      - The IP Video Management Appliance shall offer up to 12930 GB of net capacity storage.

      - The IP Video Management Appliance shall offer a bandwidth of 200 Mbit/s.

      - The IP Video Management Appliance shall offer a dual port Gigabit Ethernet network interface, 4 GB system memory and an Intel Xeon Quad Core Processor.

      - 10.	The IP Video Management Appliance shall offer remote monitoring via a desktop application or a Web browser.

- Functions

      - The IP Video Management Appliance shall offer an energy-efficient hot-swap redundant power supply.

      - The IP Video Management Appliance shall offer hot-swap SATA-II hard drives providing up to 24 TB of gross storage capacity.

      - The IP Video Management Appliance shall come pre-installed and pre-configured with all necessary software.

      - The IP Video Management Appliance shall utilize Microsoft Windows Server 2008 R2.

      - The IP Video Management Appliance shall offer Disk on Module (DoM); a solid-state, non-volatile memory module that contains a backup image of all system software needed to a full system recovery.

- Access to Video

      - The IP Video Management Appliance shall deliver high-quality HD video despite low or limited bandwidth connections.

      - The IP Video Management Appliance shall offer Dynamic Transcoding technology that retrieves data and subsequently decodes and decompresses the data stream to a lower bit stream.

      - The IP Video Management Appliance shall instantly enhance the video detail to full HD quality when the video is paused.

- D.	Management

      - The IP Video Management Appliance shall come with the VMS management application pre-installed and pre-licensed.

      - The IP Video Management Appliance shall offer the Microsoft System Center Suite built-in.

      - The IP Video Management Appliance shall allow operators to use one central tool for configuration and operations management.

- Health Monitoring

      - The IP Video Management Appliance shall provide SNMP, Remote Desktop and HTTP monitoring support.

      - The IP Video Management Appliance shall offer high-availability hardware, embedded design, and system wide monitoring.

- Storage

      - The IP Video Management Appliance shall contain eight (8) 3.5 in. SATA storage trays.

      - The IP Video Management Appliance shall have 24 TB, 2 TB SATA/3000

(7,200 RPM, 32 MB cache, 3.5 in.) hard drives installed.

      - The IP Video Management Appliance shall offer a 2108-based SAS/SATA RAID card with 8 internal ports/low profile-PCI-E.

      - The IP Video Management Appliance shall include an AMD FirePro V3900 1 GB, low profile graphics card

      - The IP Video Management Appliance shall include a Creative Sound Blaster PCI sound card.

      - The IP Video Management Appliance shall include an Intel SSD 320 OVR, 80 GB (MLC) OS drive.

### Video Management Server / Recorder (Type 4)

- General Characteristics:

      - The IP Video Management Appliance shall be a RAID-5 protected, all-in-one recording, viewing and management solution for network surveillance systems of up to 128 channels.

      - The IP Video Management Appliance shall come with a pre-installed VMS license for connecting 32 concurrent recordable cameras.

      - The IP Video Storage Appliance shall offer an optional camera expansion license for 8 additional concurrent recordable cameras up to a maximum of 128 cameras per appliance.

      - Software updates shall be available free of charge during the product warranty period. The software installed on the IP Video Management Appliance shall not be subject to any additional Software Maintenance Agreements (SMAs).

      - The IP Video Management Appliance shall utilize “enterprise-rated” hard drives in a fault tolerant RAID-5 configuration.

      - The IP Video Management Appliance shall be a pre-configured and pre-installed video management solution with up to 64 TB (8 x 8 TB) of gross storage capacity.

      - The IP Video Management Appliance shall offer up to 52136 GB of net capacity storage.

      - The IP Video Management Appliance shall offer a bandwidth of 475 Mbit/s.

      - The IP Video Management Appliance shall offer a dual port Gigabit Ethernet network interface, 8 GB system memory and an Intel Xeon Quad Core Processor.

      - The IP Video Management Appliance shall offer remote monitoring via a desktop application or a Web browser.

- Functions

      - The IP Video Management Appliance shall offer an energy-efficient hot-swap redundant power supply.

      - The IP Video Management Appliance shall offer hot-swap SATA-III hard drives providing up to 64 TB of gross storage capacity.

      - The IP Video Management Appliance shall come pre-installed and pre-configured with all necessary software.

      - The IP Video Management Appliance shall utilize Microsoft Windows Storage Server 2012 R2.

      - The Operating System of the IP Video Management Appliance shall run solid state disks in redundant configuration.

- Access to Video

      - The IP Video Management Appliance shall deliver high-quality HD video despite low or limited bandwidth connections.

      - The IP Video Management Appliance shall offer Dynamic Transcoding technology that retrieves data and subsequently decodes and decompresses the data stream to a lower bit stream.

      - The IP Video Management Appliance shall instantly enhance the video detail to full HD quality when the video is paused.

- Management

      - The IP Video Management Appliance shall come with the VMS management application pre-installed and pre-licensed.

      - The IP Video Management Appliance shall allow operators to use one central tool for configuration and operations management.

- Health Monitoring

      - The IP Video Management Appliance shall provide SNMP, Remote Desktop and HTTP monitoring support.

      - The IP Video Management Appliance shall offer high-availability hardware, embedded design, and system wide monitoring.

- Storage

      - The IP Video Management Appliance shall contain up to eight (8) 3.5 in. SATA storage trays.

      - The IP Video Management Appliance shall have up to 8 x 8 TB SATA
(7,200 RPM, 64 MB cache, 3.5 in.) hard drives installed.

      - The IP Video Management Appliance shall offer a 3108-based SAS/SATA RAID card with 8 internal ports.

      - The IP Video Management Appliance shall include an AMD FirePro W4100; 4 x Mini Display Port graphics card.

      - The IP Video Management Appliance shall include a Creative Sound Blaster PCI sound card.

      - The IP Video Management Appliance shall include 2 x 120 GB SSD drives in RAID-1 configuration

### Video Management Server / Recorder (Type 5)

- General Characteristics

      - The IP Video Management Appliance shall be a RAID-5 protected, all-in-one recording, viewing and management solution for network surveillance systems of up to 128 channels.

      - The IP Video Management Appliance shall come with a pre-installed VMS license for connecting 32 concurrent recordable cameras.

      - The IP Video Storage Appliance shall offer an optional camera expansion license for 8 additional concurrent recordable cameras up to a maximum of 128 cameras per appliance.

      - Software updates shall be available free of charge during the product warranty period. The software installed on the IP Video Management Appliance shall not be subject to any additional Software Maintenance Agreements (SMAs).

      - The IP Video Management Appliance shall utilize “enterprise-rated” hard drives in a fault tolerant RAID-5 configuration.

      - The IP Video Management Appliance shall be a pre-configured video management solution with up to 128 TB (16 x 8 TB) of gross storage capacity.

      - The IP Video Management Appliance shall offer up to 111720 GB of net capacity storage.

      - The IP Video Management Appliance shall offer a bandwidth of 475 Mbit/s.

      - The IP Video Management Appliance shall offer a dual port Gigabit Ethernet network interface, 8 GB system memory and an Intel Xeon Quad Core Processor.

      - The IP Video Management Appliance shall offer remote monitoring via a desktop application or a Web browser.

- Functions

      - The IP Video Management Appliance shall offer an energy-efficient hot-swap redundant power supply.

      - The IP Video Management Appliance shall offer hot-swap SATA-III hard drives providing up to 128 TB of gross storage capacity.

      - The IP Video Management Appliance shall come pre-installed and pre-configured with all necessary software.

      - The IP Video Management Appliance shall utilize Microsoft Windows Storage Server 2012 R2.

      - The Operating System of the IP Video Management Appliance shall run solid state disks in redundant configuration.

- Access to Video

      - The IP Video Management Appliance shall deliver high-quality HD video despite low or limited bandwidth connections.

      - The IP Video Management Appliance shall offer Dynamic Transcoding technology that retrieves data and subsequently decodes and decompresses the data stream to a lower bit stream.

      - The IP Video Management Appliance shall instantly enhance the video detail to full HD quality when the video is paused.

- Management

      - The IP Video Management Appliance shall come with the VMS management application pre-configured and pre-licensed.

      - The IP Video Management Appliance shall allow operators to use one central tool for configuration and operations management.

- Health Monitoring

      - The IP Video Management Appliance shall provide SNMP, Remote Desktop and HTTP monitoring support.

      - The IP Video Management Appliance shall offer high-availability hardware, embedded design, and system wide monitoring.

- Storage

      - The IP Video Management Appliance shall contain up to sixteen (16) 3.5 in. SATA storage trays.

      - The IP Video Management Appliance shall have up to 16 x 8 TB SATA
(7,200 RPM, 64 MB cache, 3.5 in.) hard drives installed.

      - The IP Video Management Appliance shall offer a 3108-based SAS/SATA RAID card with 8 internal ports.

      - The IP Video Management Appliance shall include an AMD FirePro W4100; 4 x Mini Display Port graphics card.

      - The IP Video Management Appliance shall include a Creative Sound Blaster PCI sound card.

      - The IP Video Management Appliance shall include 2 x 120 GB SSD drives in RAID-1 configuration

### Network Video Recorder (NVR – Type 1)

- General Characteristics

      - The IP Video Storage Appliance shall be an all-in-one recording solution for network surveillance systems of up to 16 channels.

      - The IP Video Storage Appliance shall be a pre-configured and pre-installed IP video recording solution with up to 8 TB (4 x 2 TB) storage capacity.

      - The IP Video Storage Appliance shall offer front-swappable SATA-II hard drives providing 8 TB of gross storage capacity.

      - The IP Video Storage Appliance shall run the Video Streaming Gateway to allow third-party camera integration.

      - The IP Video Storage Appliance shall allow remote viewing via the Video Security App and the Video Client.

      - The IP Video Storage Appliance shall offer a maximum of 8 TB of gross capacity storage with a corresponding 7250 GB of net storage capacity.

      - The IP Video Storage Appliance shall offer a bandwidth of 100 Mbit/s (read and write).

      - The IP Video Storage Appliance shall utilize Microsoft Windows Storage Server 2008 R2 (64-bit).

- Functions

      - The IP Video Storage Appliance shall come pre-installed and pre-configured with all necessary software.

      - The IP Video Storage Appliance shall enable viewing of high-quality HD video despite low or limited bandwidth by utilizing Dynamic Transcoding technology.

      - The IP Video Storage Appliance shall decode and decompress the data stream to a lower bit rate stream tailored to the bandwidth of the connection.

      - The IP Video Storage Appliance shall offer Disk on Module (DoM); a solid-state, non-volatile memory module that contains a backup image of all system software needed to a full system recovery.

- Management

      - The IP Video Storage Appliance shall provide a user interface for system configuration and unified appliance management.

      - The IP Video Storage Appliance shall offer the Microsoft System Center Client Suite built-in.

      - The IP Video Storage Appliance shall allow operators to use one central tool for configuration and operations management.

- Remote Viewing

      - The IP Video Storage Appliance shall provide the Video Client for remote viewing.

      - The IP Video Storage Appliance shall offer a stand-alone archive player to archive and authenticate without other workstation software.

### Network Video Recorder (NVR – Type 2)

- General Characteristics

      - The digital video recorder shall be an all-in-one recording solution for network surveillance systems of up to 32 channels.

      - The digital video recorder shall be a pre-configured and pre-installed IP video recording solution with up to 16 TB (4 x 4 TB) storage capacity.

      - The digital video recorder shall offer front-swappable SATA-II hard drives providing 16 TB of gross storage capacity.

      - The digital video recorder shall run the Video Streaming Gateway to allow third-party camera integration.

      - The digital video recorder shall allow remote viewing via the Video Security App and the Video Security Client.

      - The digital video recorder shall offer a maximum of 16 TB of gross capacity storage with a corresponding 14896 GB of net storage capacity.

      - The digital video recorder shall offer a bandwidth of 310 Mbit/s (read and write) with IP-cameras/encoders and equipped with 4 HDDs.

      - The digital video recorder shall offer an Intel Atom N3150 processer + Marvell 88SE9215 storage controller.

      - The digital video recorder shall utilize Microsoft Windows Storage Server 2012 R2 (64-bit).

      - The digital video recorder shall have tamper-protection.

      - The digital video recorder shall offer comprehensive search and playback functions.

      - The digital video recorder shall offer remote search and playback functions.

      - The digital video recorder shall allow viewing, playback and configuration via a remote Web management connection.

      - The digital video recorder shall operate a Windows based operating system.

- Functions

      - The digital video recorder shall come pre-installed and pre-configured with all necessary software.

      - The digital video recorder shall enable viewing of high-quality UHD video despite low or limited bandwidth by utilizing Dynamic Transcoding technology.

      - The digital video recorder shall decode and decompress the data stream to a lower bit rate stream tailored to the bandwidth of the connection.

      - The digital video recorder shall offer SSD; a solid-state, non-volatile memory module that contains a backup image of all system software needed to a full system recovery.

      - The digital video recorder shall have Alarm-Inputs (2) and Relay-Outputs (2).

- Recording

      - The digital video recorder shall simultaneously record a maximum 32 channels

      - The digital video recorder shall record at up to 310 Mbps per channel.

      - The digital video recorder shall allow manual and automatic recording.

      - The digital video recorder shall allow automatic recording via a schedule or based on an alarm.

- Management

      - The digital video recorder shall provide a browser-based user interface for system configuration and unified appliance management.

      - Alternatively, the digital video recorder shall allow operators to use one central tool for configuration and operations management.

- Control

      - The digital video recorder shall provide alarm inputs/outputs on the rear panel of the device.

      - The digital video recorder shall support the use of PC software or a built-in web application via a network for live viewing, playback and configuration.

      - The digital video recorder shall contain a 10/100/1000Base-T Ethernet ports for local or wide area network connection.

- Remote Viewing

      - The digital video recorder shall provide the Video Security Client for remote viewing.

      - offers its customers a connectivity service (DDNS) for access to network-connected devices without any advanced network configuration.

- Storage

      - The digital video recorder shall contain four (4) 3.5 in. SATA storage trays.

      - The digital video recorder shall have four a maximum of (4) HDD hard drives installed.

      - The digital video recorder shall include a graphics memory controller integrated in the Intel Atom N3150 processor.

      - The digital video recorder shall include a 2x1 GbE Rj45 network port.

### 22-inch High Performance HD LED Monitors

    - Performance Requirements:

      - The HD monitor shall include the following inputs: an analog RGB, a digital DVI-D, and a digital HDMI.

      - The HD monitor shall have a maximum contrast ratio of 1,000:1.

      - The HD monitor shall be capable of being mounted to a wall or placed on a desktop with an included stand.

      - The HD monitor shall support Full HD 1080p resolution (1920 x 1080).

      - The HD monitor shall offer an LED backlight panel.

      - The HD monitor shall have a viewable picture area of 22 inches.

      - The HD monitor shall automatically focus on setting the correct colour, temperature, and gamma curve settings.

      - The HD monitor shall display images using an aspect ratio of 16:9.

      - The HD monitor shall offer an active display area of (H) 476.64 mm x (V) 268.11 mm.

      - The HD monitor shall be capable of displaying 16.7 million colours.

    - Controls

      - The HD monitor shall provide a front control panel that allows the user to adjust image quality, brightness, size, position, and geometry for optimal viewing.

      - The HD monitor shall provide a front control lockout feature so that only authorized users can adjust menu settings.

      - The HD monitor shall have front panel LED indicators that convey the state of the monitor.

### 42-inch High Performance HD LED Monitors

- Performance Requirements:

      - The HD monitor shall include the following inputs: an analog RGB, a digital DVI-D, a Y/C (S-video), a loop-through video, a digital HDMI, and one BNC.

      - The HD monitor shall have a maximum contrast ratio of 4,000:1.

      - The HD monitor shall include the Trigger and Auto Switch features.

      - The HD monitor shall be capable of being mounted to a wall.

      - The HD monitor shall include a remote control device.

      - The HD monitor shall support monitor wall applications.

      - The HD monitor shall support Full HD 1080p resolution (1920 x 1080).

      - The HD monitor shall offer an LED backlight panel.

      - The HD monitor shall have a viewable picture area of 42 inches.

      - The HD monitor shall automatically focus on setting the correct color, temperature, and gamma curve settings.

      - The HD monitor shall display images using an aspect ratio of 16:9.

      - The HD monitor shall offer an active display area of (H) 930.24 mm x (V) 523.26 mm

      - The HD monitor shall be capable of displaying 1,073 million colours.

    - Controls

      - The HD monitor shall provide a rear control panel that allows the user to adjust image quality, brightness, size, position, and geometry for optimal viewing.

      - The HD monitor shall provide a rear control lockout feature so that only authorized users can adjust menu settings.

      - The HD monitor shall have front panel LED indicators that convey the state of the monitor.

### HD Decoder

- Performance Requirements:

      - As the application requires, the HD video decoder specified shall be capable of functioning on data networks, such as Ethernet LANs and over the Internet.

      - The HD decoder shall be capable of decoding high definition and standard definition streams using H.264 or MPEG-4 compression technology at up to 30 ips.

      - The HD decoder shall be capable of decoding two (2) full HD 1080p30 streams or four (4) HD 720p30 streams with up to 10 Mbps each.

      - The HD decoder shall be capable of decoding six (6) standard definition streams with up to 6 Mbps each or up to 30 video streams at a lower resolution.

      - The HD decoder shall be capable of directly driving an HD display device.

      - The HD decoder shall support the following security options:

        - Two (2) levels of password protection to prevent unauthorized connection or configuration changes to the unit.

        - [Independent AES encryption with 128‑bit keys for each communication channel – video, audio, or serial I/O – for total data protection. Requires a separate Encryption Site License.]

      - The HD decoder shall display VCA metadata.

      - The HD decoder specified shall be provided by the manufacturer complete with configuration cables, Installation and Operations Manuals, and safety instructions.

    - Decoding

      - The HD decoder shall offer the following compression options:

        - H.264 (ISO/IEC 14496-10)

        - MPEG-4

      - The HD decoder shall be capable of decoding the following stream options:

        - Four H.264 720p30 streams at 10 Mbps

        - Two H.264 1080p30 streams at 10 Mbps

        - Six H.264 standard definition streams at up to 6 Mbps

        - Twelve H.264 standard definition streams at up to 2.5 Mbps

    - Monitor Support

      - The HD decoder shall provide one DVI-I, one HDMI, and one (DP) monitor outputs (only one output can be used at a time).

      - The HD decoder shall be capable of displaying four high definition streams (720p30) in a quad-view display.

      - The HD decoder shall be capable of displaying six standard definition streams in a 2 x 3 view on a 16:9 monitor.

      - The HD decoder shall be capable of displaying up to 30 standard definition streams (at a lower resolution, bit rate, or frame rate) in a 5 x 6 view on a 16:9 monitor, arranged in selectable screen layouts.

      - The HD decoder shall be capable of switching screen layouts based on the controlling video management system or on alarm scenarios.

      - The HD decoder shall be capable of displaying six standard definition streams in a 2 x 3 view on a 16:9 monitor.

      - The HD decoder shall be capable of displaying up to 30 standard definition streams (at a lower resolution, bit rate, or frame rate) in a 5 x 6 view on a 16:9 monitor, arranged in selectable screen layouts.

      - The HD decoder shall be capable of switching screen layouts based on the controlling video management system or on alarm scenarios.

    - Mounting

      - The HD decoder shall be capable of being equipped with screw-on stands for table-top use.

      - The HD decoder shall be capable of being mounted directly to the back of monitor using the VESA mounting options of 75 mm or 
100 mm.

### HD Encoder

    - Performance Requirements:

      - As the application requires, the single-channel video encoder specified shall be capable of functioning on data networks, such as Ethernet LANs and over the Internet.

      - The encoder shall function as a server to provide H.264 video via the network to a PC workstation using a standard Web browser (such as Microsoft Internet Explorer Version 7.0 or later) as the receiver.

        - The Web browser may be used to control a or compatible camera connected to the Ethernet port of the specified encoder.

        - The web browser may also be used to configure the settings of the single-channel video encoder using the local network or via the Internet.

      - The single-channel video encoder specified may be paired with a compatible receiver to create a point-to-point IP-based connection via the network.

      - The video encoder specified shall be capable of transmitting video that can be viewed over an IP network using the Video Client or the Video Management System software running on a network workstation.

      - The video encoder shall be capable of sending both video streams to a centrally-managed recording device via a video recording manager.

      - The single-channel video encoder shall provide dual streaming capability that simultaneously creates two data streams per video input at different rates and resolution where one stream may be used for local recording and the second stream may be transmitted over the network for live viewing. (Dual streaming is dependent on the encoder settings, picture content, the amount of motion within the video, and the available computational power.)

      - The video encoder shall support video streaming as follows:

      - In a unicast function that allows communication between a single sender and a single receiver via a network.

      - In a multi-unicast mode that supports 5 simultaneously connected receivers via a network.

      - In multicast video streaming that allows communication between a single sender and multiple receivers when used in a suitably configured network using UDP and IGMP protocols.

      - The single-channel video encoder shall allow selection of the following resolutions (PAL):

704 x 576: 	4CIF: 25 ips

352 x 288:	CIF: 25 ips

      - The video encoder shall be capable of providing bi-directional audio.

      - The internal time/date clocks of the specified product shall be synchronized from the system computer or every two hours from a network time server (NTP server). The time synchronization capability ensures that simultaneously occurring events will display the correct time and date when multiple specified devices are connected to the same network.

      - The single-channel video encoder shall support the following security options:

        - Three levels of password protection to prevent unauthorized connection or configuration changes to the unit.

        - 802.1x authentication using a RADIUS server for identification.

        - Secure web browser access with HTTPS using a SSL certificate that is stored in the unit.

        - Unused access methods can be disabled to reduce risk of unauthorized access.

        - [Optionally, the video encoder shall provide independent AES encryption with 128‑bit keys for each communication channel – video, audio, or serial I/O – for total data protection. Requires a separate Encryption Site License.]

      - The single-channel video encoder shall offer built-in MOTION+ video motion detection, an algorithm based on pixel change and that includes object size filtering capabilities and sophisticated tamper detection capabilities.

      - The video encoder shall offer optional embedded Video Content Analysis (VCA) based on the Intelligent Video Analysis (IVA) algorithm. This algorithm shall be based on digital imaging technology that uses multi-level image analysis of pixel, texture and motion (trajectory) changes.

      - The single-channel video encoder shall provide one standard BNC connectors for connection of the video input sources.

      - The single-channel video encoder shall be compatible with NTSC, PAL, EIA, and CCIR video sources.

      - The video encoder shall allow recording to an internal SD card.

      - The video encoder shall allow recording to an external iSCSI target.]

      - The video encoder shall allow recording of two independent streams simultaneously, being recorded on the same or different recording media.

      - The video encoder shall allow having its iSCSI storage medium managed by Video Recording Manager (VRM).

      - PTZ control of a or compatible camera connected to the serial interface port of the specified encoder shall also be available when used with the Video Client or the Video Management System software.

      - Video clips from the video sequence of any camera input of the encoder currently being displayed on the browser may be saved on the PC hard drive.

      - The encoder specified shall be provided by the manufacturer complete with configuration cables, Installation and Operations Manuals, and instructions to download and install all the required software for the unit’s operation such as MPEG Active X control, an MPEG viewer, DirectX viewer, etc.

      - The single-channel video encoder shall conform to Profile S as defined by the Open Network Video Interface Forum (ONVIF) specification.

### Indoor/Outdoor Day/Night HD 2 Mega Pixels IP Vari-Focal  Dome  camera with PoE (Wide dynamic range)

    - General Characteristics:

      - The vandal resistant HD camera shall be capable of operating in an indoor or an outdoor environment.

      - The vandal resistant HD camera shall utilize a 1/2.7-inch CMOS HD image sensor.

      - The vandal resistant HD camera shall offer a 3-9 mm or a 10-23 mm vari-focal, super resolution lenses with an advanced iris design.

      - The vandal resistant HD camera shall have high light sensitivity

      - The vandal resistant HD camera shall offer Content-based Imaging Technology (C-BIT).

      - The vandal resistant HD camera shall utilize Intelligent Dynamic Noise Reduction (iDNR) technology to reduce the bitrate and storage requirements by removing noise artifacts.

      - The vandal resistant HD camera shall produce a resolution of 1920 x 1080 pixels (HD 1080p) at 30 ips with a 16:9 image format.

      - The vandal resistant HD camera shall produce a resolutions 1280 x 960 (960p HD) and of 704 x 480 (D1) pixels at 30 ips with a 4:3 image format.

      - The vandal resistant HD camera shall provide direct network connection using H.264 and JPEG compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.

      - The vandal resistant HD camera shall provide a CVBS (PAL), 1 Vpp, BNC, 75 Ohm analog output that allows hybrid video output.

      - The vandal resistant HD camera shall be rated to IP 66 (NEMA Type 4X) standard against water and dust ingress.

      - The vandal resistant HD camera shall be rated to IK10 impact protection (the equivalent of 55 kg).

      - The vandal resistant HD camera shall work with Power over Ethernet IEEE 802.3af (802.3at Type 1).

      - The vandal resistant HD camera shall support AutoMDIX.

      - The vandal resistant HD camera shall conform to the ONVIF Profile S specification.

      - A user shall be able to view video on a PC using a Web browser, with the Video Management System, Video Client, Recording System, or with the Video Security iPad App.

      - The vandal resistant HD camera shall provide six configurable user modes that provide optimized settings for distinct applications.

      - The vandal resistant HD camera shall offer Intelligent Video Analysis (IVA).

      - The vandal resistant HD camera shall provide four independent, fully programmable privacy mask areas.

      - The vandal resistant HD camera shall provide an on-screen display to simplify the camera/lens back focus and network configuration settings.

      - The vandal resistant HD camera shall provide enhanced night viewing through the increase of IR sensitivity by automatically switching a motorized IR filter from color to monochrome operation in low-light or IR illuminated applications. Allow the IR filter to be switched manually via the alarm input, preprogrammed in a camera mode or profile.

      - The vandal resistant HD camera shall utilize pixel-by-pixel analysis to automatically compensate for bright areas of a high contrast scene (Back light) without having to define a window or area.

      - The vandal resistant HD camera shall provide intelligent Auto Exposure (iAE) to improve visibility of dark objects against a light background and vice versa. Use IVA to detect in which parts of the image local contrast enhancement can improve image usability.

      - The vandal resistant HD camera shall offer intelligent Dynamic Noise Reduction to reduce bandwidth and storage requirements by optimizing the detail-to-bandwidth ratio via temporal and spatial noise filtering.

      - The vandal resistant HD camera shall offer two regions of interest to zoom into a specific area of the full image.

      - The vandal resistant HD camera shall allow regions of interest to be sent in separate streams so it is possible to view both an overview and a detail at the same time.

      - The vandal resistant HD camera shall offer a digital WDR of 76 dB.

      - The vandal resistant HD camera shall provide a frame integration mode that can increase the integration time up to 10 times on the CMOS sensor.

      - The vandal resistant HD camera shall provide enhanced night viewing through the increase of IR sensitivity by automatically switching a motorized IR filter from color to monochrome operation in low-light or IR illuminated applications. Allow the IR filter to be switched manually via the alarm input, preprogrammed in a camera mode or profile.

      - The vandal resistant HD camera shall utilize pixel-by-pixel analysis to automatically compensate for bright areas of a high contrast scene (Back light) without having to define a window or area.

    - Video Streaming

      - The vandal resistant HD camera shall deliver multiple H.264 video streams and an M-JPEG stream.

      - The vandal resistant HD camera shall offer an upright streaming mode that delivers an image of 400 x 720 (9:16 aspect ratio) that is cropped from the full sensor image.

    - Storage Management

      - The vandal resistant HD camera shall support iSCSI devices to allow video stream to be recorded directly to an iSCSI RAID array.

      - The vandal resistant HD camera shall support iSCSI storage targets to enable the camera to function as a conventional DVR.

      - The vandal resistant HD camera shall have a microSD card slot that uses standard; off-the-shelf microSD (SDHC and SDXC) cards for local storage (up to 2 TB).

      - The local storage feature shall be capable of storage for Automatic Network Replenishment (ANR).

### Indoor Day/Night IP Corner Mount No-Grip vandal proof Camera

    - Performance Requirements

      - The camera shall be Integrated Day Night active-infrared type.

      - The camera shall incorporate IP Infrared Imaging (i3) design to optimize the combined benefits of IP and infrared illumination for critical imaging applications.

      - The camera shall have IP network capability.

      - The camera shall provide daytime color performance.

      - The camera shall provide night-time active-infrared monochrome performance.

      - The camera shall have a 2:1 interlaced scanning system.

      - The camera shall be vandal resistant.

      - The camera shall be designed to be gripless and anchor-free for maximum safety

      - The camera shall operate with high reliability.

    - Performance:

      - The camera shall be able to view the entire floor and all four walls of a 4.5 metre square room, including the two walls to which it is attached.

      - The camera shall have no exposed wiring or anchor points, making it highly vandal-resistant and suitable for suicide watch.

      - The camera shall have a 1/3” LXR CCD for experimeterent IR sensitivity, low smear, low streak and experimeterent anti-blooming characteristics

      - The camera shall have a 1/3” CCD with mechanical filter technology for vivid daytime color and effective night-time performance under infrared illumination.

      - The camera shall incorporate automatic switching between day and night modes.

      - The camera design shall eliminate the possibility of focus shift to ensure accurate focus for a daytime average wavelength of 500nm and a night-time average wavelength of 850nm.

      - The camera shall produce accurate color representation by eliminating IR bleed and/or other color distortions.

      - The camera shall produce outstanding contrast characteristics for reduced glare and streaking.

      - The camera shall have separate camera and LED voltage regulator boards for increased electrical stability and reliability.

    - Mechanical:

      - The camera housing shall be a robust aluminum casting.

      - The camera shall have a black or white baked enamel finish.

      - The camera shall be ruggedized for vandal resistance.

      - The camera shall be in a “truncated tetrahedron” shape ensuring a flush installation into ceiling/wall corners.

      - The camera shall be designed to compensate for the walls and ceiling being out of “square” by as much as 3°.

      - The camera shall have no exposed wiring or anchor points, making it highly vandal-resistant and suitable for suicide watch.

      - The camera shall incorporate a 45° tilted face to enable viewing of entire rooms, including directly underneath the camera itself.

      - The camera housing shall be equipped with two separate windows, one for IR light transmission and the other for CCD video imaging.

      - The camera shall have 1/4 in. (6 mm) Lexan windows and be fully supported with by continuously bolted-down metal back plate.

      - The camera shall be available with an optional hidden microphone module for audio recording.

### Day/Night HD 2 Mega Pixels IP vari-Focal box cameras with PoE (Wide dynamic

### range)

    - General Characteristics:

      - The camera shall utilize a 1/2.7-inch CMOS HD image sensor.

      - The camera shall offer Content-based Imaging Technology (C-BIT).

      - The camera shall utilize Intelligent Dynamic Noise Reduction (iDNR) technology to reduce the bitrate and storage requirements by removing noise artifacts.

      - The camera shall provide direct network connection using H.264 and JPEG compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.

      - The camera shall work with Power over Ethernet IEEE 802.3af (802.3at type 1) for indoor applications with a compliant power supply source.

      - The camera shall support AutoMDIX.

      - The camera shall conform to the ONVIF Profile S specification.

      - A user shall be able to view video on a PC using a Web browser, with the Video Management System, Video Client or Recording Station.

      - The camera shall provide MOTION+ video motion detection analysis system that provides basic video content analysis.

      - The camera shall provide six configurable user modes that provide optimized settings for distinct applications.

      - The camera shall offer Intelligent Video Analysis (IVA).

      - The camera shall provide four independent, fully programmable privacy mask areas.

      - The camera shall provide an on-screen display to simplify the camera/lens back focus and network configuration settings.

      - The camera shall provide enhanced night viewing through the increase of IR sensitivity by automatically switching a motorized IR filter from color to monochrome operation in low-light or IR illuminated applications. Allow the IR filter to be switched manually via the alarm input, preprogrammed in a camera mode or profile.

      - The camera shall utilize pixel-by-pixel analysis to automatically compensate for bright areas of a high contrast scene (Back light) without having to define a window or area.

      - The camera shall provide intelligent Auto Exposure (iAE) to improve visibility of high contrast scenes (dark objects against a light background and the reverse). Use IVA to detect in which parts of the image local contrast enhancement can improve image usability.

      - The camera shall offer intelligent Dynamic Noise Reduction to reduce bandwidth and storage requirements by optimizing the detail-to-bandwidth ratio via temporal and spatial noise filtering.

      - The camera shall offer regions of interest to zoom into a specific area of the full image.

      - The camera shall allow regions of interest to be sent in separate streams so it is possible to view both an overview and a detail at the same time.

      - The camera shall provide enhanced night viewing through the increase of IR sensitivity by automatically switching a motorized IR filter from color to monochrome operation in low-light or IR illuminated applications. Allow the IR filter to be switched manually via the alarm input, preprogrammed in a camera mode or profile.

      - The camera shall utilize pixel-by-pixel analysis to automatically compensate for bright areas of a high contrast scene (Back light) without having to define a window or area.

      - The camera shall accept CS and C mount type lenses and detect automatically the type of lens used and optimize performance accordingly.

      - The camera shall provide a lens wizard for local or remote control of the motorized lens back focus system to allow focusing at maximum lens opening to ensure that the objects of interest within the field of view always remain in focus.

      - The camera shall provide a multi-language on-screen display.

    - Storage Management

      - The camera shall support iSCSI devices to allow video stream to be recorded directly to an iSCSI RAID array.

      - The day/night IP camera shall support iSCSI storage targets to enable the camera to function as a conventional DVR.

      - The day/night IP camera shall have a microSD card slot that uses standard; off-the-shelf microSD (SDHC and SDXC) cards for local storage (up to 2 TB).

      - The local storage feature shall be capable of storage for Automatic Network Replenishment (ANR).

      - The camera shall provide email alarm messaging with optional JPEG posting.

      - The camera shall offer Embedded Intelligent Video Analytics (IVA).

    - Intelligent Video Analysis

      - The camera shall be capable of processing and analyzing video within the camera itself, with no extra hardware required.

      - The camera shall be capable of detecting and sending alarms for abnormal events.

      - The camera shall allow users to set up to 10 separate profiles and switch profiles based on a day/night or holiday schedules.

### Indoor Day/Night IP Vandal-proof Speed Dome cameras

    - Performance Requirements:

      - The HD PTZ camera shall be a full-featured HD PTZ unit designed for discrete video surveillance applications in indoor environments.

      - The HD PTZ camera shall offer enhanced system flexibility with dual recording (iSCSI and SD card) options.

      - The HD PTZ camera shall provide Intelligent Tracking to continuously track objects in motion.

      - The HD PTZ camera shall offer a Wide Dynamic Range of 86 dB for clear images in extreme high-contrast environments.

      - The HD PTZ camera shall provide direct network connection using H.264 and JPEG compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.

      - The HD PTZ camera shall offer embedded Intelligent Video Analysis (IVA) that eliminates dedicated PCs and associated software maintenance.

      - The HD PTZ camera shall conform to the ONVIF standard to provide interoperability with other conformant systems.

      - The HD PTZ camera shall offer configurable quad streaming with individually configurable HD streams.

      - The HD PTZ camera housing shall be a durable, rugged design with an acrylic bubble.

    - Imaging:

      - The HD PTZ camera shall have a minimum working distance of 10 mm (wide) to 150 mm (tele).

      - The HD PTZ camera shall offer a Sodium Vapour White Balance mode that automatically compensate for light from a sodium vapour lamp to restore objects to their true colour.

    - Image Processing:

      - The HD PTZ camera shall provide an AutoScaling feature that reduces the pan/tilt speed as the camera zooms in on an object, so that the relative speed on the screen remains constant.

    - System Features:

      - The HD PTZ camera shall allow an optional fibre optic media converter module designed to accept a wide-range of 10/100 Mbps SFP modules for use with Multimode or Single mode optical fibre with LC or SC connectors.

      - The HD PTZ camera PTZ camera shall be compatible with the Video Client and the Video Management System.

    - Pre-programmed Modes:

      - The HD PTZ camera shall offer 5 pre-programmed but configurable user modes.

      - The pre-programmed modes shall be optimized with the best settings for the following environments:

        - Outdoor

        - Indoor

        - Low Light

        - Motion

        - Vibrant

      - The HD PTZ camera shall allow users to customize these modes for the specific requirements of the camera site.

    - Recording and Storage Management:

      - The HD PTZ camera shall support iSCSI devices to allow video stream to be recorded directly to an iSCSI RAID array.

      - The HD PTZ camera shall support iSCSI storage targets.

      - The HD PTZ camera shall have an SD card slot that uses a standard, off-the-shelf SD (Secure Digital), SDHC (Standard Digital High Capacity) or a SDXC (Secure Digital eXtended Capacity) card for local storage (up to 2 TB).

      - The HD PTZ camera shall be compatible with the Video Recording Manager to control and manage video recording

    - Intelligent Video Analysis:

      - The HD PTZ camera shall be capable of processing and analyzing video within the camera itself, with no extra hardware required.

      - The HD PTZ camera shall be capable of detecting and sending alarms for abnormal events.

      - The HD PTZ camera shall be configurable to analyze up to 10 different scenes for one or more of the following events: Line Crossing, Loitering, Idle Object, Removed Object, Conditional Change, Trajectory Tracking, and Filters.

      - The HD PTZ camera shall allow users to set up to 10 separate profiles and switch profiles based on a day/night or holiday schedules.

      - The HD PTZ camera shall support scene tours that automatically reposition the camera to each scene for a specified duration.

      - The HD PTZ camera shall support Bird’s Eye View (BEV) people counting.

      - The HD PTZ camera shall incorporate an Alarm Rule Engine, enabling abnormal events that IVA detects to prompt the camera to take one or more actions such as:

        - Trigger a relay connected to an alarm siren and/or strobe

        - Trigger a visual alert to be displayed on the operator’s screen

        - Go to a specified scene (pre-set position)

    - Motion Tracking:

      - The HD PTZ camera shall offer Intelligent Tracking to continuously track an object using pan, tilt, and zoom actions.

      - The HD PTZ camera shall provide automatic motion tracking using intelligent video analytics.

      - The HD PTZ camera shall have the ability to follow an object continually when passing behind a privacy mask.

      - The HD PTZ camera shall allow a user to define virtual masks for a scene so certain objects are not considered for flow analysis and will not trigger Intelligent Tracking.

      - The HD PTZ camera shall offer the following control options for the Intelligent Tracking feature:

        - Off – the HD PTZ camera does not track moving object.

        - Auto – the HD PTZ camera actively analyzes the video to detect moving objects.

        - One Click – the HD PTZ camera allows a user to click a moving object in the live video image to activate Intelligent Tracking.

        - IVA-triggered – the HD PTZ camera continuously analyzes the scene for IVA alarms or an IVA rule violation. If an alarm or rule violation is detected, the camera activates Intelligent Tracking to track the object that triggered the alarm or rule violation.

      - The HD PTZ camera shall have the ability to restart tracking if a target starts moving in the same area where the initial target stopped moving or if the camera detects an object moving along the last known trajectory.

      - The HD PTZ camera shall allow an operator to select an object to track in the live image view.

      - The HD PTZ camera shall automatically start tracking a target that violates an IVA rule or triggers an IVA alarm.

    - Housing Options:

      - The HD PTZ camera shall provide built-in surge protection for power, data, and video and alarm inputs.

      - The HD PTZ camera dome bubble shall:

        - Be a high-resolution acrylic bubble.

        - Offer a clear or tinted version.

      - The indoor/outdoor pendant housing shall:

        - Conform to the NEMA 4X standard for the following:

        - Access to Hazardous parts

        - Ingress of solid foreign objects (falling dirt, circulating dust, settling dust)

        - Ingress of water (dripping and light splashing, hosedown and splashing)

        - Corrosive agents

### Outdoor Day/Night IP Vandal-proof Speed Dome cameras

    - Performance Requirements

      - The HD PTZ camera shall be a full-featured HD PTZ unit designed for discrete video surveillance applications in outdoor environments.

      - The HD PTZ camera shall provide Intelligent Tracking to continuously track objects in motion.

      - The HD PTZ camera shall provide full HD 1080p and 720p resolutions.

      - The HD PTZ camera shall offer a Wide Dynamic Range of 86 dB for clear images in extreme high-contrast environments.

      - The HD PTZ camera shall provide direct network connection using H.264 and JPEG compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.

      - The HD PTZ camera shall offer embedded Intelligent Video Analysis (IVA) that eliminates dedicated PCs and associated software maintenance.

      - The HD PTZ camera shall conform to the ONVIF standard to provide interoperability with other conformant systems.

      - The HD PTZ camera shall generate multiple simultaneous video streams:

        - High Definition Streams:

          - 1 H.264 1080p30 or 720p60 stream plus 1 I-frame stream plus 1 M-JPEG simultaneously

          - 1 independently configurable H.264 720p30 stream plus 1 independently configurable H.264 Baseline Plus (BP+) or H.264 Main Profile Standard Definition (MP SD) plus 1 I-frame plus 1 M-JPEG video stream simultaneously

        - Standard Definition Streams:

1 H.264 BP+ or H.264 MP SD stream plus 1 H.264 BP+ or H.264 MP SD stream plus 1 I-frame stream plus 1 M-JPEG stream simultaneously

      - The HD PTZ camera housing shall be a durable, rugged design with an acrylic bubble.

    - General Characteristics:

      - The HD PTZ camera shall support the following tour modes:

        - 99 user-defined pre-positions with 20-character titles.

        - 1 preset tour capable of 99 pre-positions and a configurable dwell time between positions.

        - 1 Auto-Pan mode.

      - The HD PTZ camera shall provide pan and tilt preset repeatability accurate to within ±0.1 degrees.

      - The HD PTZ camera shall provide the following variable pan/tilt speeds

        - A range of 0.1 degrees per second to 120 degrees per second.

        - A pan speed of 360 degrees per second and a tilt speed of 100 degrees per second between prepositions.

      - The HD PTZ camera shall provide a tilt range of 0 to 94 degrees and a pan range of up to 360 degrees of continuous rotation.

      - The HD PTZ camera shall provide 24 individual privacy masks with the following features:

        - Shapes shall be defined with four corners.

        - The mask shall be gray.

      - The HD PTZ camera dome bubble shall:

        - Meet flame, crush, and impact resistant requirements able to exceed UL 746C standard for polymeric material enclosures.

        - Be a high-resolution bubble made of acrylic.

        - Offer a clear or tinted version.

    - Basic Features:

      - The HD PTZ camera shall provide a feature that automatically rotates, or pivots, the camera to simplify tracking of a person walking directly under the camera.

      - The HD PTZ camera shall provide advanced troubleshooting and diagnostics via diagnostic LEDs and on-screen diagnostic displays.

      - The HD PTZ camera shall allow an optional integral fibre optic media converter transceiver module, capable of transmitting and receiving video and Bi-phase signals up to 60 km.

      - The day/night IP PTZ camera shall be compatible with the Video Client and the Video Recording Manager.

    - Housing Options:

      - The HD PTZ camera shall be offered with an Outdoor Pendant housing.

      - The HD PTZ camera housings shall come standard with recessed setscrews and a recessed bubble latch for increased tamper resistance.

      - The HD PTZ camera shall provide built-in surge protection for power, data, and video and alarm inputs.

      - The Outdoor pendant housing shall:

        - Come with an attached sunshield.

        - Allow camera to view 18º above the horizon.

        - Conform to IP66 and NEMA 4X standards for a rugged and weather-resistant package.

        - Use a low-impact, high-resolution acrylic bubble.

    - IP Connectivity:

      - The HD PTZ camera shall allow full camera control and configuration capabilities over the network.

      - The HD PTZ camera shall be capable of capturing and storing images using H.264 compression at HD 1080p and HD 720p resolutions.

      - The HD PTZ camera shall deliver DVD-quality 1080p video, at rates up to 30 images per second, via TCP/IP over Cat5/Cat6 UTP cable.

      - The HD PTZ camera shall support iSCSI devices to allow the network-enabled camera to stream video directly to an iSCSI RAID array.

      - The HD PTZ camera shall conform to the ONVIF standard.

      - The HD PTZ camera shall conform to the NTCIP 1205 protocol.

      - The HD PTZ camera shall offer embedded Intelligent Video Analysis (IVA) that eliminates dedicated PCs and associated software maintenance.

    - Intelligent Video Analysis:

      - The HD PTZ camera shall be capable of processing and analyzing video within the camera itself, with no extra hardware required.

      - The HD PTZ camera shall be capable of detecting and sending alarms for abnormal events.

      - The HD PTZ camera shall be configurable to analyze up to 10 different scenes for one or more of the following events: Line Crossing, Loitering, Idle Object, Removed Object, Conditional Change, Trajectory Tracking, and Filters.

      - The HD PTZ camera shall allow users to set up to 10 separate profiles and switch profiles based on a day/night or holiday schedules.

      - The HD PTZ camera shall support scene tours that automatically reposition the camera to each scene for a specified duration.

      - The HD PTZ camera shall incorporate an Alarm Rule Engine, enabling abnormal events that IVA detects to prompt the camera to take one or more actions such as:

        - Trigger a relay connected to an alarm siren and/or strobe

        - Trigger a visual alert to be displayed on the operator’s screen

        - Go to a specified scene (preset position)

    - Motion Tracking:

      - The HD PTZ camera shall offer Intelligent Tracking to continuously track an object using pan, tilt, and zoom actions.

      - The HD PTZ camera shall provide automatic motion tracking using intelligent video analytics.

      - The HD PTZ camera shall have the ability to follow an object continually when passing behind a privacy mask.

      - The HD PTZ camera shall have the ability to restart tracking if a target starts moving in the same area where the initial target stopped moving or if the camera detects an object moving along the last known trajectory.

      - The HD PTZ camera shall allow an operator to select an object to track in the live image view.

### IR ILLUMINATOR

    - Performance Requirements:

      - The infrared illuminator shall use reduced power consumption.

      - The infrared illuminator shall use high-efficiency surface mount LEDs.

      - The infrared illuminator shall produce even illumination for a balanced distribution of light across a scene and depth-wise with asymmetric horizontal beam patterns of 10°, 20°, 30°, 60°, 95° and 120°.

      - The infrared illuminator shall produce vertical beam patterns of 10º for all asymmetric horizontal beam patterns except for the horizontal beam pattern of 95º where the vertical beam pattern shall be 14º and the horizontal beam pattern of 120º where the vertical beam pattern shall be 17º.

      - The infrared illuminator shall eliminate hotspots in the foreground and underexposed backgrounds with 3D Diffuser technology.

      - The infrared illuminator shall produce even illumination with uniformity of less than 55% variation across field of illumination.

      - The infrared illuminator shall enable increased surveillance range, wider beam patterns, and evenly illuminated nighttime surveillance with 3D Diffuser technology.

      - The infrared illuminator shall produce an illumination level of typical center power no less than 0.3μm/cm2 at the tested distances listed in Section C Performance Range.

      - The infrared illuminator shall have Constant Light technology that provides a constant light output over the lifetime of the product.

      - The infrared illuminator shall feature an on-board microprocessor to monitor LED feedback and output.

      - The infrared illuminator shall have a constant light output when operated at an ambient temperature of -40°C to +50°C.

      - The infrared illuminator shall enable optimal night-time performance of megapixel cameras, pan-tilt cameras, speed domes and other critical surveillance applications.

      - The infrared illuminator shall enable proper night-time function of video analytics and other intelligent video software.

      - The infrared illuminator shall have a built-in, sensitivity adjustable photoperimeter for automatic on / off operation.

      - The infrared illuminator shall be switchable by an external device via a built-in telemetry input.

      - The infrared illuminator shall have a built-in relay output to trigger another device when switching on / off.

    - General Characteristics:

      - The infrared illuminator shall be a solid state LED type.

      - The infrared illuminator shall provide illumination from 30 m to 320 m.

      - The infrared illuminator shall be designed to IP66 for operation in harsh weather conditions.

      - The infrared illuminator shall have been tested for outdoor usage.

      - The infrared illuminator shall be powered by a universal, low voltage Class II power supply.

    - Construction:

      - The infrared illuminator shall be compact, robust and sealed for performance under all weather conditions.

      - The infrared illuminator shall have a solid state design without any moving mechanical parts.

      - The infrared illuminator shall be made of robust aluminum casting and extrusion.

      - The infrared illuminator shall have a black finish.

      - The infrared illuminator shall operate independently of any cooling fan or similar device, either internal or external.

      - The infrared illuminator shall dissipate thermal energy through an integral heat sink.

      - The infrared illuminator shall be supplied with 4 m high-temperature power cable.

    - Environmental:

      - The infrared illuminator shall have a pressure equalization valve to ensure reliable long term environmental performance.

### Thermal IP Camera

    - Performance Requirements

      - The Thermal Security Camera shall not depend on any visible or invisible (infrared) illumination or image intensifier to “see” i.e. produce images.  The Thermal Security Camera shall be totally passive and not produce any energy or emit light in any bandwidth.  The Thermal Security Camera shall allow the user to clearly identify images in the total absence of light.

      - The Thermal Security Camera shall allow the user to see through smoke and light fog and to view the thermal patterns and contrast in the scene.

      - The Thermal Security Camera shall utilize a Vanadium Oxide (VOx) uncooled microbolometer responding in the LWIR (Long Wave Infrared) spectral range of 7.5 – 13.5 μm which is beyond what is visible to the human eye.

      - The Thermal Security Camera shall not be susceptible to permanent damage after imaging the sun.

      - The Thermal Security Camera shall not utilize shutters to prevent damage from the sun.

      - The Thermal Security Camera shall include a lens or window that is temperature controlled to prevent dew, frost and ice accumulation.

      - The Thermal Security Camera shall not utilize dynamic apertures to protect the image sensor because these mechanisms reduce sensitivity for an extended period of time, thus reducing the Thermal Security Camera performance as required for security installations.

      - The Thermal Security Camera shall provide a thermal optics that automatically adjust to ambient temperature changes, and therefore do not require re-adjustment and/or thermal refocusing.

      - The Thermal Security Camera shall not be susceptible to “image blooming” caused by bright lights as are image intensifiers and visible spectrum cameras.

      - The Thermal Security Camera shall be available with fixed anti-reflection coated Germanium lenses with the Field of View (FOV) and resolutions.

      - The range of the Thermal Security Camera shall be defined at three levels consisting of:

##### Detection – In order to detect if an object is present or not, its critical dimension needs to be covered by 1.5 or more pixels.

##### Recognition – Recognizing an object is defined as seeing what type of object it is.  This means being able to determine if the object is a person, a car or a truck.  In order to recognize an object it needs to be subtended by at least 6 pixels across its critical dimension.

##### Identification – Identifying the object is defined as seeing if it is a man/woman or a man carrying a shovel verses a man carrying a rifle.  In order to identify an object it needs to be subtended by at least 12 pixels.

      - The Thermal Security Camera image sensor with a clear aperture f/1.0 lens shall provide a NETD of <50mK.

      - The Thermal Security Camera shall include Auto Digital Detail Enhancement (Auto DDE) which is an advanced non-linear image processing algorithm.  The Auto DDE shall enhance the image detail to match the total dynamic range of the original image allowing details to be visible to the user even in scenes with low or high thermal contrast.  Auto DDE shall increase the probability of detection of low contrast images.

      - The Thermal Security Camera shall utilize Non-Uniformity Correction (NUC) which is a set of compensation factors for each pixel.  NUC shall enable the following features and benefits:

##### Eliminate the need for FPA (Focal Plane Array) temperature stabilization.

##### Allow for near instantaneous camera turn-on.

##### Reduced system complexity and power consumption.

##### Allow for a wider operating temperature range.

      - The Thermal Security Camera shall include Automatic Gain Control (AGC) circuitry to compensate for scene variations, improve image quality by avoiding saturation and distortion, and to balance signal levels prior to display to maximize image quality.

      - The Thermal Security Camera shall have a Wide Dynamic Range (WDR) capability to compensate for scenes that include extreme temperature ranges (such as when the sun is in the FOV) without losing details in the terrestrial foreground.

      - The Thermal Security Camera shall feature both White-Hot and Black-Hot operating modes.  In the White-Hot (default) mode warmer images shall be displayed in white or lighter shades than cooler or background areas.  In the Black-Hot mode warmer objects shall be displayed as black or dark gray compared to cooler objects.

      - The Thermal Security Camera shall provide standard PAL analog composite video output (factory configured) to allow it to function as a direct replacement for daylight camera and to connect directly to digital video recorders, encoders and monitoring equipment.  The analog video signal shall be available via a BNC video output connector.

      - The Thermal Security Camera shall provide a local analog video output connector (RCA type).  This feature shall allow the installer to test the Thermal Security Camera and view live video during installation and set-up without interrupting the main video output to the overall security system.

      - The Thermal Security Camera outdoor enclosure with sunshield and mounting base shall meet IP66 and IP67 rating for dust and water ingress.

      - All cable connections shall be made inside of the enclosure.  The enclosure shall be provided with liquid-tight sealed cable gland fittings for analog video, Ethernet, serial control, and power cables.

      - The camera enclosure shall include grounding and surge protection.  A separate Earth ground connection shall be made inside the enclosure to a designated grounding lug.  The Earth ground conductor may be run as part of the power cable bundle.

      - The Thermal Security Camera shall meet vibration testing according to IEC 60068-2-27: 10g shock pulse with a 11ms half- sine profile.

      - The Thermal Security Camera shall feature an IP network interface, built-in Ethernet port, built-in web browser interface / Nexus server for device set-up, configuration and control.

      - The Thermal Security Camera shall provide two independent IP network streams (channels) of user selectable MPEG-4, H.264 or M-JPEG digital video.

      - The thermal security camera shall be ONVIF compliant and provide an IP network interface that is based on open standards to insure compatibility with a wide range of third-party video players and Video Management Systems.

      - The Thermal Security Camera shall operate as a hybrid device by providing both analog video (NTSC or PAL) simultaneously with IP video.  This dual-mode operation will allow the camera to provide video to both analog and IP networks at one time.

### IP License Plate Camera

    - General Characteristics:

      - The license plate capture camera shall be specially designed to capture high-quality images of vehicle license plates.

      - The license plate capture camera shall feature offer analog and IP models.

      - The license plate capture camera shall include infrared illumination.

      - The license plate capture camera shall filter out visible light and eliminate the effects of headlight glare.

      - The license plate capture camera shall minimize plate overexposure from sunlight for more accurate automatic license plate recognition.

      - The license plate capture camera shall include adjustable imaging modes to fine-tune the imager for specific regions or license plate recognition algorithms.

      - The license plate capture camera shall integrate with the Digital Video Recorder, the Video Management System, and with the Video Client.

      - The license plate capture camera shall integrate with third-party ANPR software.

    - Analog Imager Requirements

      - The analog imager shall utilize a technology with a 1/3-inch monochrome CCD image sensor capable of producing up 540 TVL of resolution.

      - The analog imager shall be fitted with a 5-50 mm varifocal lens.

      - The analog imager shall offer one fully programmable video motion detection area.

      - The analog imager shall offer four fully programmable, independent privacy masks.

      - The analog imager shall produce a composite video signal, via a BNC connector, for service or maintenance purpose that allows a direct input to conventional analog CCTV video equipment.

      - The analog imager shall provide an on-screen display to simplify the illumination, and network configuration settings.]

    - IP Imager Requirements

      - The IP imager shall offer one fully programmable video motion detection area.

      - The IP imager shall offer four fully programmable, independent privacy masks.]

      - The IP imager shall provide direct network connection using H.264 (ISO/IEC 14496-10); M-JPEG, and JPEG compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.

      - The IP imager shall offer Power over Ethernet Plus (IEEE 802.3at class 4) support.

      - The IP imager shall conform to the ONVIF standard

    - License Plate Capture Requirements

      - The license plate capture camera shall utilize the Night Capture Imaging System.

      - The Night Capture Imaging System shall provide a burst of infrared illumination and simultaneously filter out visible light.

      - The license plate capture camera shall utilize Advanced Ambient Compensation.

      - Advanced Ambient Compensation shall utilize high-intensity pulsed infrared illumination and an ultra fast shutter.

      - The license plate capture camera shall be capable of capturing the following nominal plate widths (with 4CIF encoding over capture range): 130 pixels

      - The license plate capture camera shall be capable of capturing the following usable plate widths (with 4CIF encoding over capture range): 100 to 170 pixels

      - 7.	The license plate capture camera shall be optimized to capture: 520 x 115 mm (approximate) license plates.

      - The license plate capture camera shall be equipped with an 850nm pulsed LED array IR illuminator.

      - The license plate capture camera shall have a capture range of 3.8 to 28.0 m.

      - The license plate capture camera shall have an optimal distance of 4.9 m to 21.3 m

      - The license plate capture camera shall be capable of capturing clear plate images from vehicles moving at speeds up to 225 km/h at 30° mounting angle.

    - General Requirements

      - The license plate capture camera shall provide power, video, and control via an Ethernet connection

      - The license plate capture camera shall provide a built-in test pattern generator.

      - The license plate capture camera shall provide a multi-language on-screen display.

      - The IP imager shall allow full camera control and configuration capabilities over the network except for mechanical adjustments.

      - The IP imager shall be capable of capturing and storing images using H.264 and JPEG encoding and compression at 4CIF/D1 and CIF resolutions.

      - The IP imager shall deliver DVD-quality 4CIF video, at rates up to 30 images per second, via TCP/IP over Shielded Cat5/Cat6 cable. Leverages bandwidth throttling and multicasting capabilities to manage bandwidth and storage requirements efficiently while delivering the best possible image quality and resolution.

      - The IP imager shall generate two independent H.264 streams, an I-frame recording stream, and an M-JPEG stream simultaneously.

      - The IP imager shall support iSCSI devices to allow video stream to be recorded directly to an iSCSI RAID array.

      - The IP imager shall conform to the ONVIF standard.

## NETWORK BACKBONE SYSTEM

### Ring Topology

- The network shall be based on a ring topology. The connections of the different devices shall occur via optical fibres cables. Optical fibre cables shall reduce the cable weight and shall increase the quality of the transmitted signals. Electromagnetic interference and cable capacity shall be no issue. Optical fibres shall be thin, light weighted and flexible. For example, a 150m rugged environment cable rolled up on a special rubber cable drum shall weigh 5.3 kg. The cables shall require very little space; installation shall become easy and comfortable.

- The network and its optical fibre connections shall offer the highest standards in regard to control and complexity. Control signals such as the network control remote data, third party control and Ethernet data, word clock signals or video shall be included and send using the same fibre cable as used for the audio signals. No additional RS422, RS485 or Ethernet cables shall be necessary for controlling. Troubleshooting shall become easy.

- A ring network topology shall be suitable to build in redundancy. The dual redundant ring structure of the network shall provide maximum safety in a comprehensible network with an extreme low system latency below 42μs. The transmission delay shall be constant from any point to any point. Galvanic isolation between the devices shall be provided, therefore, ground loops shall not exist.

- The network system shall offer a large number of cost-effective devices to facilitate the use and the advantages of fibre optical digital data transmission in all sorts of temporary and permanent applications, especially when long distance connections and high-quality audio shall be required. The network system shall provide devices capable to digitally transport signals such as Fast Ethernet, MADI, RS422, RS485, DMX and MIDI. In addition audio, video and data signals shall be transmitted via optical fibre. The devices shall include bidirectional composite video and word clock interfaces. The module shall offer word clock input and output. The module should provide extension for a main fibre ring with a Synchronous Network over Cat5. Redundant power supply and safeguards against malfunctions shall be provided through dual power supply units with automatic switchovers. The digital I/O devices shall include two optical 1/2 Gbps SFP LINK interfaces with duplex LC-connectors.

### 24 SFP Ports, (2) 10/100/1000 RJ-45 Ports, (2) Gigabit Ports Managed Layer 3 Ethernet Switches

    - DESCRIPTION

      - The Gigabit TP / SFP combo ports can be either 10 / 100 / 1000Mbps on TP ports or 1000Base-SX / LX only through the SFP (Small Form-Factor Pluggable) interface.

      - The SFP module shall utilize 850nm optics capable of bi-directional data transmission of 1000Base-SX on two multimode optical fibers.

      - The SFP module shall utilize 1310nm optics capable of bi-directional data transmission of 1000Base-LX on two single-mode optical fibers.

      - The SFP module shall utilize 1310nm/1490nm or 1310nm/1550nm optics capable of bi-directional data transmission of 1000Base-BX on one single-mode optical fiber.

      - The SFP module shall utilize 1310nm optics capable of bi-directional data transmission of 100Base-FX on multimode or single-mode optical fibers.

    - GENERAL SPECIFICATIONS

      - The switch shall comply with IEEE 802.3, 802.3u, 802.3ab and 802.3z Ethernet standard.

      - The switch shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.

      - The switch shall support the transmission of 100 Mbps over a multimode or single-mode fiber.

      - The switch shall support the transmission of 1000 Mbps over a multimode or single-mode fiber.

      - The switch shall provide a RS-232 serial connection for local management of the device.

      - The switch shall be connected with Cat 5/5e/6 UTP/STP cable system for its RJ-45 interface ports.

      - The switch shall provide power, link speed and fiber port status indicating LED’s for monitoring proper system operation.

### Industrial 8-Port 10/100/1000T 802.3at PoE + 2-Port 100/1000X SFP Managed Switch with Wide Operating Temperature (Field Switch)

    - DESCRIPTION

      - The PoE Industrial Switch shall provide 8 10/100Mbps Fast Ethernet ports and 2 Gigabit TP/SFP combo interfaces with 8 full powered PoE ports (no port sharing) delivered in a rugged high-strength case.

      - The PoE in-line power shall be compliant with the IEEE 802.3af standard providing 15.4W per port that can power devices at a distance up to 100 meters through the 4-pair Cat 5/6 UTP wire.

      - Full PoE per IEEE802.3af standards (15.4 W) shall be provided to each of the 8 ports with no PoE sharing between ports.

      - The Gigabit TP / SFP combo ports shall be either 10 / 100 / 1000Mbps on TP ports or 1000Base-SX / LX only through the SFP (Small Form-Factor Pluggable) interface.

      - The SFP module shall utilize 1310nm optics capable of bi-directional data transmission of 100Base-FX on multimode or single-mode optical fibers.

      - The SFP module shall utilize 850nm optics capable of bi-directional data transmission of 1000Base-SX on two multimode optical fibers.

      - The SFP module shall utilize 1310nm optics capable of bi-directional data transmission of 1000Base-LX on two single-mode optical fibers.

      - The SFP module shall utilize 1310nm/1490nm or 1310nm/1550nm optics capable of bi-directional data transmission of 1000Base-BX on one single-mode optical fiber.

      - The PoE Industrial Switch shall be an industrially hardened and fully managed Ethernet Switch specifically designed to operate reliably in electrically harsh and climatically demanding environments.

    - GENERAL SPECIFICATIONS

      - The module shall support the transmission of up to 2 or 3 channels of 100 Mbps over a multimode or single-mode fiber.

      - The module shall support the transmission of up to 2 or 3 channels of 1000 Mbps over a multimode or single-mode fiber.

      - The module shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.

      - The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.

      - The module shall provide power, power fault, Ring master, link speed, and fiber port status indicating LED’s for monitoring proper system operation.

      - The module shall have redundant power supply connections to minimize single point failure.

      - The module shall provide a RS-232 serial connection for local management of the device.

### Managed 24 Port 10/100 Field Switch with PoE

    - DESCRIPTION

      - The Layer 2 Managed PoE Switch shall provide 24 10/100TX ports with IEEE 802.3af PoE and 2 Gigabit TP/SFP combination ports.

      - The PoE in-line power shall be compliant with the IEEE 802.3af standard providing 15.4W per port that can power 24 PoE compliant devices at a distance up to 100 meters through the 4-pair Cat 5/5e UTP wire

      - The Gigabit TP / SFP combo ports shall be either 10 / 100 / 1000Mbps on TP ports, or, 1000Base-SX / LX only through SFP (Small Form-Factor Pluggable) interface.

      - The SFP module shall utilize 850nm optics capable of bi-directional data transmission of 1000Base-SX on two multimode optical fibers.

      - The SFP module shall utilize 1310nm optics capable of bi-directional data transmission of 1000Base-LX on two single-mode optical fibers.

      - The SFP module shall utilize 1310nm/1490nm or 1310nm/1550nm optics capable of bi-directional data transmission of 1000Base-BX on one single-mode optical fiber.

    - GENERAL SPECIFICATIONS

      - The switch shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.

      - The switch shall comply with IEEE 802.3af Power over Ethernet.

      - The switch shall support IEEE802.3af Power over Ethernet detection and 48VDC power injection from port#1 to port#24.

      - The switch shall transmit DC Voltage to the Cat5/5e cable and transfer data and power simultaneously to remote PD (Powered Device) equipment.

      - The module shall Auto-detect PoE IEEE 802.3af equipment; protect devices from being damaged by incorrect installation.

      - The switch shall provide power, link speed, PoE In-use and fiber port status indicating LED’s for monitoring proper system operation.

      - The switch shall provide a RS-232 serial connection for local management of the device.

      - The switch shall be connected with Cat 5/5e/6 UTP/STP cable system for its RJ-45 interface ports.

      - The switch shall support a total distance of up to 100 meters on each PoE port.

### Managed 24 Port 10/100/1000 Core Switch

    - DESCRIPTION

      - The Layer 3 Managed Gigabit Ethernet Switch shall provide 24 Gigabit ports with 4 shared mini-GBIC SFP combination ports.

      - The shall be equipped with 2 dedicated High-Speed HDMI-like interfaces for stacking management.

      - The PoE in-line power shall be compliant with the IEEE 802.3af  standard providing 15.4W per port that can power up to 24 PoE compliant devices at a distance up to 100 meters through the 4-pair Cat 5/5e UTP cable.

      - The Gigabit TP / SFP combo ports can be either 10 / 100 / 1000Mbps on TP ports or 1000Base-SX / LX only through the SFP (Small Form-Factor Pluggable) interface.

- The SFP module shall utilize 850nm optics capable of bi-directional data transmission of 1000Base-SX on two multimode optical fibers.

- The SFP module shall utilize 1310nm optics capable of bi-directional data transmission of 1000Base-LX on two single-mode optical fibers.

- The SFP module shall utilize 1310nm/1490nm or 1310nm/1550nm optics capable of bi-directional data transmission of 1000Base-BX on one single-mode optical fiber.

- The SFP module shall utilize 1310nm optics capable of bi-directional data transmission of 100Base-FX on multimode or single-mode optical fibers.

    - GENERAL SPECIFICATIONS

      - The switch shall comply with IEEE 802.3, 802.3u, 802.3ab and 802.3z Ethernet standard.

      - The switch shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.

      - The switch shall support the transmission of 100 Mbps over a multimode or single-mode fiber.

      - The switch shall support the transmission of 1000 Mbps over a multimode or single-mode fiber.

      - The switch shall provide a RS-232 serial connection for local management of the device.

      - The switch shall be connected with Cat 5/5e/6 UTP/STP cable system for its RJ-45 interface ports.

      - The switch shall support IEEE802.3af Power over Ethernet detection and 48VDC power injection at port#1 to port#24.

      - The switch shall transmit DC Voltage to the Cat5/5e cable and transfer data and power simultaneously to remote PD (Powered Device) equipment.

      - The switch shall Auto-detect of PoE IEEE 802.3af equipment; protect devices from being damaged by incorrect installation.

      - The switch shall support a total distance up to 100 meters on each PoE port.

      - The switch shall provide power, Stack group master, Stacking interfaces, FAN alert, link active, PoE In-use and fiber port status indicating LED’s for monitoring proper system operation.

### Transceivers Modules

    - DESCRIPTION

      - Performance Requirements: Provide a MSA Compliant Small Form-Factor Pluggable (SFP) Optical Device.

      - The devices shall utilize 850/1310/1550 nm optics capable of simultaneous bi-directional signal transmission on one or two multimode optical fibers.

      - The devices shall utilize 1310/1550 nm optics capable of simultaneous bi-directional signal transmission on one or two single mode optical fibers.

    - GENERAL SPECIFICATIONS

      - The interchangeable SFP modules shall be available for use with copper media, or multimode and single mode optical fiber.

      - The optical fiber SFP modules shall be available in fast Ethernet one and two fiber versions and Gigabit one and two fiber versions.

      - They also shall be available with LC or SC optical connectors.

      - The SFP modules shall have different wavelengths and optical power to offer distances from 300 meters to 120 kilometers.

      - The module shall require no in-field electrical or optical adjustments or in-line attenuators to ease installation.

      - The module shall have an MTBF of >100,000 hours.

      - All LED indicators and both electrical and mechanical connections shall be identified with silk-screened labels.

      - The module shall have a lifetime warranty to reduce system life cycle cost in an event of a module failure.

## PERIMETER INTRUSION DETECTION SYSTEM

### kinematic intrusion detection system

    - System description

      - The system shall be a kinematic intrusion detection system for perimeter protection.

      - The system shall incorporate distributed, fence mounted kinematic detection devices.

      - The system shall incorporate rack/ or DIN rail mounted system controller (head end), suitable for indoor or outdoor location.

      - The system shall incorporate a twisted pair field device cable, linking detection devices with the controller.

      - The system will measure the kinematic energy in the fence structure as a result of disturbances, caused by intrusion.

      - The system shall be able to detect disturbances caused by attempts to breach the fence.

      - The system shall be capable of locating the point of intrusion.

      - The system performance shall not be degraded by the accumulated environmental noise on the section of fence.

      - Discrete, independent detection devices shall be used to monitor each section of fence.

      - The system shall provide a controller (head end), hosting multiple connections on a TCP/IP network for monitoring, control and maintenance of the system.

      - The controller shall be based on industrial imbedded processor.

      - The parameters on the alarm processing unit shall be adjustable in both the amplitude and frequency domain on an individual sensor basis for both the cutting and removing or moving of the fence and detection components.

      - The system shall be commissionable to allow for maximum probability of detection (POD), minimal nuisance alarms (NAR) and false alarms (FAR).

      - Each sensor shall be individually addressable.

      - The operator shall be able to identify the device that caused the alarm within a sector or zone.

    - SYSTEM COMPONENTS

- Field components shall include

      - Kinematic detection devices (D-2-21 units)

      - Device link cable

      - Installation hardware

    - Head end components

      - Power supply

      - Power interface and surge protection

      - System controller

      - Processor module

      - Device link interface module

      - Outdoor enclosure or Equipment rack

      - Control software

      - Interface software

    - SYSTEM PERFORMANCE

      - The Fence disturbance detection units (sensors) shall be based on kinematics principles detecting climbing, cutting or removal of components of the Fence.

      - This detection unit shall be installed directly on the perimeter fence attached to the fence structure by means of a dedicated bracket.

      - The required detection shall be based on direct measurement of the causes of cutting and removing of the structure and not derivatives thereof.

      - Detection shall be based on the measurement of the kinematical behaviour of the structure during intrusion attempts.

- Detection Principles

The system shall sense the level and frequency of kinematic disturbance created by an intrusion.

The system shall monitor the operational status of each detection device.

The detection devices shall be attached to the fence at regular intervals, to detect disturbances of the fence.

The sensitivity of measurement shall depend on the spacing between detection devices.

- Factors Affecting System Performance

System performance will depend on the fence construction, and sensor spacing.

The following factors may increase rates of nuisance alarms:

        - Loose fence posts and struts

        - Loose fence fabric

        - Loose signs

        - Loose swing gates

The system shall have variable detection parameters to allow for adjustment to achieve the best balance between probability of detection and nuisance alarm rate.

The system performance shall depend on the nature (intensity and duration) of the intrusion, and the detection settings

- Detectable Intrusions

Intrusion attempts where posts and struts are used to support climbing.

Intrusion attempts resulting in direct climbing, cutting, spreading and lifting of the fence fabric.

Intrusion attempts that do not result in contact with the fence, such as bridging and tunnelling shall not be detectable.

- Probability of Detection

The system shall generate and report an alarm with greater than 95% probability for an isolated breach attempt in quiet environment that involves direct and prolonged contact with the fence structure and results in the intruder’s crossing of the fence line.

Such breaches shall include those attempted by direct climbing, cutting, spreading, and lifting of the fence or fence fabric.

- Time to Detection

The system shall generate an alarm within one second from conclusion of detection algorithm. This period excludes delays as a result of attack count and hold-off parameter settings.

- Accuracy of Intrusion Location

The location of intrusion shall be determined by detection device spacing.

The location of intrusion shall be reported with an accuracy of better than twice the distance between two adjacent devices.

- False Alarms

The false intrusion alarms generated due to occurrences excluding routine maintenance shall be limited to less than one such alarm per month of continuous operation

- Nuisance Alarms

Nuisance alarms shall be limited by spacing the sensors to achieve a disturbance signal strength, caused by intrusion that is substantially larger than the worst expected environmental disturbance.

Depending on the sensitivity setting of the sensors a guideline should be less than 1 per zone per month.

    - System description

The kinematic sensor shall function as an electronic perimeter intrusion detector. The system shall be used in conjunction with weld mesh fences to protect the perimeter of a site. The system shall consist of kinematic sensors and a device link and head-end. The system shall be capable of monitoring different styles of metal fabric fencing such as chain-link, expanded-metal or welded-mesh fence.

The sensor shall detect intruders by utilizing signals generated by kinematic behaviour of the fence caused by attempting to cut, climb, or raise the fence fabric. The system shall be capable of functioning as a integral part of a centralized control and maintenance site.

    - System technology

The sensor shall analyze the signals from the fence detect kinematic behaviour in the fabric of the fence. The processor shall utilize adaptive algorithms, ambient signal compensation and selectable common-mode rejection, to discriminate between actual, false and nuisance alarms, without lowering the probability of detection. The sensor shall have independent adjustments and thresholds for each type of intrusion and shall have the capability reject nuisance alarms.

    - KINEMATIC SENSOR

- Detection device

The detection device shall be rated for outdoor-use.

The device shall be designed to be mounted on a fence structure.

The device shall be made of UV resistant material.

The device shall have a lifetime of more than 10 years.

- Device link cable

The device link cable shall be a solid core twisted pair copper cable.

The outer jacket shall be made of black UV resistant polyethylene.

The device link cable shall have a life time of more than 10 years.

The device link cable shall be rated for exposed installation on the fence, or for installation in conduits.

The outside diameter of the cable shall be approximately 5mm diameter.

- Sector Length

The system shall be capable of monitoring a total length of up 500meter (cable length) per device link.

Each node may contain up to 32 device links.

Each device link may service up to 32 devices.

- Sensor Layout

Sensors can be deployed on a perimeter as a uniform distribution on the fence or with gaps at buildings, gates and other discontinuities.

- Environmental Specifications

The field detection equipment shall withstand operation temperatures between -20°C and 70°C.

The field detection equipment shall operate within said temperature range without performance degradation.

    - KINEMATIC SENSOR INSTALLATION

- Fence Requirements

Fence construction shall conform to industry standards for security fences.

Fence shall be properly maintained.

A clearance area shall be present on both sides of the fence.

Gates shall be secured in the closed position without any play.

The fence fabric shall be properly secured to the structure.

- Detection Device

Detection devices shall be mounted to the fence structure or fence fabric in such a way to ensure the transfer of kinematic energy from the fence to the device.

Devices may be installed inside approved enclosures, containing cable terminations.

The position of the detection device on the fence shall depend on the fence type. Typical spacing between sensors on various fence types will be as follows:

| Fence type | Cutting, Sawing, Grinding | Unassisted Climbing |
| --- | --- | --- |
| Weld-mesh (typical 100mm by 50mm aperture, 3mm wire thickness, high tensile) | 9m | 6m |
| Weld-mesh (smaller than above aperture same wire dimensions) | 12m | 9m |
| Chain-link (50mm by 50mm aperture) | 15m | 9m |
| Steel palisade (with steel posts) | 9m | 6m |

Typical position shall be on the secure side at a height of at least 500mm.

Fasteners used shall be compatible with the material of the fence and detection device / enclosure.

- Device Link Cable

The method of installation shall include the following:

Inside a conduit, or

Attached to the fence fabric, using UV stabilised nylon cable ties.

    - SYSTEM HEAD END

- Head End Components

- Components

- Controller module

- Ethernet communications module

- Device link module

- Power supply interface module

- Head End Specifications

- All components are DIN rail mountable

- All modules are multiples of standard DIN-rail sizes

- Embedded controller module 2U

- Ethernet communications module – 4U

- Device link module – 2U

- Power supply interface module – 4U

- Power supply – 4U

- Total Head End DIN rail space required = 30U

- Power Requirements

Head end requires a 24Vdc 100W supply

- Environmental Specifications

- Field sensors

- Hermetically sealed

- Submersible

- -10 to 70 degrees Celsius

- Other units

- Must be installed in an IP65 rated enclosure

- -10 to 70 degrees Celsius

- System Interface

TCP – interface: The Head end has a TCP interface that will allow a front end system or 3rd party equipment to get alarms from the head end, or control states on the head end

User Interface: UI software that will graphically represent the state of the perimeter can be made available to the end user

    - SYSTEM SOFTWARE

- Kinematic Sensor

Each kinematic sensor has a processor that applies a detection algorithm to the disturbances observed by the sensing element. The sensor will then determine whether or not an alarm has occurred and report this condition accordingly. The parameters of this detection algorithm can be adjusted by means of diagnostic software on a PC.

- Head End

Functionality

- Alarm Handling

All alarm events that are detected by the sensors are reported to the head end. The user interface (connected to the head end) will cycle through various states according to detection events and user interaction. Typical states are Normal->Alarm->Alarm Reason. Each state will be represented by a unique colour on the area of the perimeter that has been affected.

- Event Logging

All maintenance conditions, alarm conditions and operator behaviour that occur on the system are logged on the head end. These logs will be made available through a log utility.

- Graphics and Site Layout

The head end contains a digital representation of the site map and all zones on the perimeter. This representation is shown to the user via the UI software. The user will see a map of the perimeter with all zone states in real time.

- Diagnostics and Setup

Diagnostic and setup tools will be available to

a.	Define sensor configuration

b.	Set up controller configuration

c.	Verify system operation

d.	Analyse alarms

- Remote Interface

All software tools communicate to physical hardware via the Ethernet interface provided by the Ethernet communications module. This means that the system tools can be used from any remote location that has a UDP and TCP connection to the head end.

    - WARRANTY AND SERVICE

The system shall be free of defects in workmanship and material under normal operating conditions for a period of one year from the date of shipping.

Any parts shown defective in workmanship or material during the warranty period shall be repaired, replaced or adjusted free of charge.

Local or locally represented service organization shall maintain trained and certified manpower adequate for the service needs of the installed system.

Warranty and general service shall be provided locally by an approved service provider as per OEM’s terms and conditions.

### Advanced Acoustic Detection System

## System description

The digital microphonic cable fence disturbance sensor shall function as an electronic perimeter intrusion detector. The system shall be used in conjunction with fences to protect the perimeter of a site. The system shall consist of an ultraviolet resistant triboelectric transducer cable, and a microprocessor based dual zone digital signal processor. The system shall be capable of monitoring different styles of metal fabric fencing such as chain-link, expanded-metal or welded-mesh fence. The sensor shall detect intruders by utilizing signals generated by the minute flexing of the triboelectric transducer cable, caused by attempting to cut, climb, or raise the fence fabric. The system shall be capable of functioning as either a standalone system or as an integral part of a centralized control and maintenance facility.

## System technology

The digital signal processor shall analyze the signals from the triboelectric transducer cable and shall detect minute vibrations in the fabric of the fence. The processor shall utilize adaptive algorithms, ambient signal compensation and selectable common-mode rejection, to discriminate between actual, false and nuisance alarms, without lowering the probability of detection. The processor shall identify, by type, a cut intrusion and a climb intrusion. The sensor shall have independent adjustments and thresholds for each type of intrusion and shall have the capability to completely mask climb or cut alarms.

## Microphonic cable

The cable transducer shall be an ultraviolet resistant triboelectric sensor cable and shall be attached to the fence by means of ultraviolet resistant cable ties. The cable shall generate signals when an attempt is made to cut, climb, or lift the fence fabric.

## Signal processing algorithms

The system shall utilize digital signal processing techniques that employ adaptive algorithms, capable of adapting to specific fence types and environmental conditions.

## Detection sensitivity

The system shall detect intruders climbing, lifting or cutting the fence while rejecting other environmental stimuli. The sensitivity level shall be adjustable for each zone’s specific conditions.

## Probability of detection

The probability of detection (PD) for an intruder cutting the fence, and for unaided climbing attempts shall be 95% with a 95% confidence factor.

## System-generated alarms (False alarms)

The maximum rate for alarms generated by internal electronic processes (cables excluded) shall be less than one per zone per year, averaged over the total number of zones in the system.

## Zone length

The maximum length of each zone shall be 305 m of sensor cable. Individual zone length shall be determined by the physical boundaries of each zone. The sensor cable shall be supplied in rolls of 305 m and shall be cut to the correct length at the time of installation.

## Gates

The sensor shall be capable of monitoring or bypassing swinging and sliding gates by using a Gate Bypass Module. The system shall be capable of placing monitored gates in access mode (no alarm when the gate is used), or secure mode within a secure zone, by either local or remote command. The status of the gate (secure or access) shall be communicated by relay contacts.

## Distributed processing

The signal processors distributed along the perimeter shall receive and process the signals from the sensor cables while providing fail-safe operation. The failure of one processor shall not affect the signal processing of the other processors along the perimeter.

## Total sensor cable length

Total sensor cable length shall be expandable from the 610m maximum using one signal processor to an unlimited length using multiple processors. The detection zone shall be continuous and uniform, and there shall be no gap between the individual zones, when installed in accordance with the manufacturer’s recommendations.

## Alarm outputs

The digital signal processor shall identify intrusion, and supervision alarms locally by relay contacts. Each alarm zone shall include one intrusion alarm relay and one supervisory alarm relay. Each dual zone processor shall include four alarm output relays.

Alarms caused by climbing, cutting, or otherwise disturbing the fence fabric shall be identified as intrusion alarms. Intrusion alarms shall activate their respective alarm relay (zone 1 or zone 2) and shall be distinguished from supervisory alarms.

Alarms caused by power failure, low input voltage, internal electronic fault, or opening the outer enclosure (tamper) shall be identified as supervisory alarms. These supervisory alarms shall activate both of the dual zone processor’s supervisory alarm relays. Alarms caused by cable faults shall be identified as supervisory alarms. Cable fault supervisory alarms shall activate their respective supervisory alarm relay (zone 1 or zone 2). Supervisory alarms shall be distinguished from intrusion alarms.

## Reliability/maintainability

The signal processor shall have a mean time between failures (MTBF) of greater than 40, 000 hours and a mean time to replace (MTTR) of less than 10 minutes.

## Physical installation criteria

When installed outdoors, the signal processor shall be mounted in a weatherproof, fiberglass, NEMA 4 rated enclosure. The processor shall be properly grounded with a user-supplied ground rod that is separate from the fence or pole upon which the processor is mounted. The enclosure shall include a hinged cover that is capable of being locked by a user-supplied pad lock. The enclosure shall include a tamper device. The enclosure shall include mounting feet that can be installed on the enclosure to suit the size and type of mounting pole or surface.

## Mounting location

The enclosure shall be mounted on a wall, fence, or pole, separate from the fence on which the sensor cables are mounted, on the secure side of the perimeter.

## Sensor calibration

Each sensor zone shall be capable of being calibrated from its respective signal processor. Sensor calibration shall be made using a configuration module, which shall allow the technician to adjust and monitor the response of each zone. The configuration module shall be detachable via a snap-in connector and shall be capable of calibrating each of the processors in the system. The configuration module shall receive power from the processor and shall not require batteries, calibration or maintenance. Accessing the snap-in connector shall require the opening of the processor’s enclosure. This action shall cause a tamper alarm to be generated.

## Calibration parameters

The following system parameters shall be adjustable by the user:

  - Cut detection: independent threshold, count and time per zone

  - Climb detection: independent threshold, duration and time per zone

  - Preamp gain: to match the fence to the sensor

## Restricted calibration parameters

The following system parameters shall be adjustable by the user, through the use of a restricted pass-code. These parameters shall only require adjustment for highly specialized applications:

  - Ambient compensation: enable/disable, level (for background effects)

  - Common mode rejection: enable/disable (for environmental effects)

  - Peak trigger value: to identify intrusion over background

  - Cut profile value: to better define a cut event over environmental effects

  - Alarm output relay activation time: between 0.5 s and 5.0 s

## System installation and commissioning

The system shall be installed and commissioned in accordance with the manufacturer’s recommended procedures as defined in the product’s installation and setup guides.

Prior to installation, the installer shall have completed a manufacturer’s training program and be certified by the manufacturer. Alternatively, the installer shall be required to have the manufacturer, or their designate, provide qualified technical support for installation and commissioning.

Acceptance tests shall be performed in accordance with standard procedures available from the manufacturer.

## Recalibration requirements

There shall be no need to recalibrate the system after initial calibration except as the fence condition deteriorates (loose fence elements or wires).

## 4.2	Sensor cable repair

If the sensor cable is cut or damaged, it shall be capable of being repaired using additional cable, if required, and an appropriate splice kit. The splice kit shall require the use of only standard tools (i.e. slot screwdriver, wire strippers, wire cutters).

## RAISED ACCESS FLOOR SYSTEM

    - System Description

Assemblies shall be composed of modular and self-supporting floor sub-structure bolted together, having gravity placed floor panels on top not connected to the pedestal supports. Lateral strength of floor system shall be independent from floor panels being in place, or fully removed.

    - Performance Requirements

Structural Performance:

Provide access flooring system capable of withstanding the following loads and stresses within limits and under conditions indicated, as determined by testing manufacturer's current standard test procedures:

  - Concentrated Loads:

Provide 600x600mm floor panels, including those with cutouts, capable of withstanding a concentrated design load of 5000N, with a top-surface deflection under load and a permanent set not to exceed, respectively, 3.3 mm and 0.2 mm. If custom size floor panels are provided with a span of less or equal to 800 mm between secondary support beams, they need to comply with the above deflection and permanent set values as well, except if located under installed equipment cabinets or racks.

  - Rolling Loads:

Provide 600x600mm floor panels, capable of withstanding a rolling load of 6350N, with a top-surface deflection under load and a permanent set not to exceed, respectively, 3.3 mm and 0.2 mm.

  - Uniform Distributed Loads:

Provide self-supporting floor structure, without panels in place, capable of withstanding a minimum 10 kN/m2 uniform distributed load. For heavy equipment, which requires higher loading in accordance with the engineering drawing, the floor structure shall provide a uniform distributed loading capable of supporting the equipment for each individual case to avoid using separate equipment stands under Server racks or cabinets.

  - Ultimate* Loads:

Provide access flooring sub-structure system capable of withstanding a minimum ultimate concentrated load of 9070 N and a minimum ultimate distributed load of 39 kN/m2 without failing

* = max deflection of L/360 of span between beam sections

  - Pedestal Axial Load Test:

Provide structure and pedestal assemblies, without panels in place, capable of withstanding a 40 500 N axial load per pedestal.

  - Recycled content:

Understructure system and floor panel shall be required to have a minimum recycled content of 75%.

- *ESD-Control Properties:

Provide floor coverings with ESD-control properties indicated as determined by testing identical products per test method indicated by an independent testing and inspecting agency.

- Antistatic Floor Covering Properties:

- Electrical Resistance: Test per EN 14041, 2004.

- Greater than 50,000 ohms and an average value of less than 50.000 megohm when test specimens and installed floor coverings are tested surface to ground resistivity at a relative humidity of 50%.

- .Static Generation: Max 100 V when tested at 50 percent relative humidity with conductive footwear.

* ESD: Electrostatic discharge. The transfer of electric charge between bodies at different potentials, from panel surface to ground.

    - PRODUCTS

- Floor Panels, General: Provide modular panels complying with the following requirements that one person, using a portable lifting device, can interchange with other field panels without disturbing adjacent panels or understructure:

- Nominal Panel Size: 600x600 mm. Custom size panels to be as specified based on engineering drawing.

- Fabrication Tolerances: Fabricate panels to the following tolerances with square ness tolerances expressed as the difference between diagonal measurements from corner to corner:

Size and Square ness: Plus or minus 0.38 mm of required size, with a squareness tolerance of plus or minus 0.38 mm, unless tolerances are otherwise indicated for a specific panel type.

- Flatness: Plus or minus 0.50 mm, measured on a diagonal on top of panel.

- Panel attachment to Understructure: By gravity.

- Wood-Core Panels with metal backside: Fabricate from 38 mm thick, V313 moist resistant and E1 type particleboard core, made with <10 ppm urea formaldehyde. Laminate bottom aluminum face sheet with a direct laminate process using heat and pressure, providing a flame-spread index of 25 or less per ASTM E84 or NFPA 266. Provide tapered core edges including direct laminated surface finish of M335 Granite décor. All panel edges should be enclosed with a 0.45 mm glued perimeter ABS edge trim. Edge trim shall be applied so it covers the tapered panel edges, including surface finish. Provide custom panel sizes under equipment unless “open bottom access” is specified using a 38 mm steel tube under front and back of the equipment if shown on engineering drawings. Provide custom panels if shown on engineering drawings to assure all panels in service aisles or cooling aisles are fully removable.

- Perforated Airflow Panels: Perforated Triad steel airflow panels designed for static loads of. shall be interchangeable with standard field panels and shall have 25% to 56% open surface area with the following air distribution capability:

- Floor understructure: Assembly shall consist of 80x40 mm primary and secondary layer tube steel beam sections bolted together 90 degrees perpendicular to each other with angle clips and self tapping screws. Tube steel sections shall provide a yield and a tensile strength to meet the max allowed temporary deflection of L/360 of span. A distributed and concentrated static load calculation report shall be furnished for approval by certified structural engineer. All primary sections shall have a tension screw plate mounted to one side for tension against the perimeter wall. Provide “open bottom access” under the equipment racks using a square 38 mm steel tube under front and back of the equipment aisle if shown on engineering drawings.

- Pedestals: Assembly consisting of base 80x40 mm tube column and head cap including head bracket with provisions for height adjustment, made of steel.

- Base: Rectangular base with not less than 75 cm2. of bearing area.

- Column: Of height required to bring finished floor to elevations indicated, less 200 mm. Pressed securely into base plate and head cap.

- Provide vibration-proof leveling mechanism for making and holding fine adjustments in height over a range of not less than +/- 25 mm and for locking at a selected height, so deliberate action is required to change height setting and vibratory displacement is prevented.

- Head: Designed to support head bracket indicated which is attached to primary stringer.

Rust corrosion, metal components: All parts of the Floor under   structure including Pedestal components shall be hot-dipped galvanized to ensure that no zinc particles will erode into the atmosphere.

- Floor Panel Coverings

General: Provide factory-applied direct laminate by raised access flooring manufacturer to top surface of floor panels.

Standard Direct Laminate:

Manufactured from phenolic and melamine resin impregnated papers, using a separate, high-wear type melamine glass overlay.

Wear resistant to >6000 cycles according to EN 438-2:6 1991.

Fabricate to cover each panel face prior to applying edge trim.

- Accessories

- Nail plugs: Manufacturer's standard nail plugs for securing pedestal bases to sub floor if nothing else is shown on the engineering drawings. Glue should not be used.

- Cutouts: Provide cutouts in floor panels for cable grommets and service outlets. Provide reinforcement or additional support, if needed, to make custom size panels or cutouts to comply with standard performance requirements.

- Fit cutouts with manufacturer's standard grommets in sizes indicated or, if size of cutouts exceeds maximum grommet size available, trim edge of cutouts with manufacturer's standard plastic molding or edgetrim. Furnish removable covers for grommets if specified.

- Ramps: Manufacturer's standard ramp construction of width and slope indicated, but not steeper than 1:12, with non-slip floor covering to match the same performance and construction requirements as of the access flooring, or as indicated on the engineering drawings.

- Railings: Standard extruded-aluminum railings, at ramps and open-sided perimeter of access flooring where indicated. Include handrail, intermediate rails, posts, brackets, end caps, wall returns, wall and floor flanges, plates, and anchorages where required, or as indicated on the engineering drawings.

- Panel Lifting Device: Manufacturer's standard portable lifting device of double type required for specified panels. Provide one lifting devices including wall mounted panel lifting bracket or a number as otherwise specified.

- Perimeter Support: Where indicated, provide manufacturer’s standard method for supporting panel edges and forming transition between access flooring and adjoining floor coverings. Perimeter support covering shall match floor panel finish(es), or as indicated on the engineering drawings.

    - EXECUTION

- Examination

- Examine substrates, for compliance with requirements for installation tolerances and other conditions affecting performance of work.

- Verify that substrates comply with tolerances and other requirements specified in other Sections and that substrates are free of cracks, ridges, depressions, scale, foreign deposits, and debris. Verify that concrete slab sub floor has been sealed.

- Proceed with installation only after unsatisfactory conditions have been corrected.

- Preparation

Lay out floor panel installation to keep the number of cut panels at floor perimeter to a minimum. Avoid using panels cut to less than 8 inches (200 mm).

Complete any necessary sub floor preparation, and vacuum clean sub floor to remove construction debris before beginning installation.

- Installation

- Install access flooring system and accessories under supervision of access flooring manufacturer's authorized and certified representative to produce a rigid, firm installation that complies with performance requirements and is free of instability, rocking, rattles, and squeaks.

    - Installation, Phase I

- Install primary beam sections supported by and mounted to pedestal assemblies so that no interference with feeder cables to and from equipment racks or cabinets occurs.

- Set pedestals with nail plugs as recommended by access flooring manufacturer to provide full bearing of pedestal base on sub floor.

- Level sub-structure pedestals supporting primary beam sections to permit panels be level and to proper height as set out in engineering drawings. Secure the leveling by tightening the locking nuts on all pedestals.

- Install secondary beam sections supported by primary beam sections using angle clips and self-tapping screws, so that they line up center to center with all panels in accordance with the manufacturers floor layout drawings.

- Before installation phase II starts, perform cable management, electrical and HVAC installations under the floor substructure to prevent floor panels to be removed and reinstalled by subcontractors. By following this procedure, project schedule can be shortened and damage of floor panels be avoided.

    - Installation, Phase II

- Install floor panels securely in place, properly seated with panel edges flush. Do not force panels into place. Verify if custom size panels are to be located in rows where equipment racks or cabinets of different depths are to be installed, to allow for service aisle panels to be fully removable.

- Scribe perimeter panels to provide a close fit with adjoining construction using foam tape between perimeter panel and wall, with no voids greater than 6 mm where panels abut vertical surfaces.

- Cut and trim access flooring and perform other dirt-or-debris-producing activities at a remote location, or as required to prevent contamination of sub floor under access flooring already installed.

- Ground flooring system as recommended by manufacturer and as needed to comply with performance requirements for electrical resistance of floor system and coverings.

- Clean dust, dirt, and construction debris caused by floor installation, and vacuum sub floor area, as installation of floor panels proceeds.

- Install access flooring without change in elevation between adjacent panels and within the following tolerances:

- Plus or minus 1.5 mm in any 3 meter distance.

- Plus or minus 3 mm from a level plane over entire flooring area.

- Adjusting, Cleaning, And Protection

- Prohibit traffic on access flooring structure unless floor panels have been installed, or floor structure is covered by secure means to prevent accidents.

- After completing installation, vacuum clean access flooring and cover with continuous sheets of reinforced paper or plastic if required. Maintain protective covering until time of Substantial Completion.

- Replace access floor panels that are stained, scratched, or otherwise damaged or that do not comply with specified requirements.

- After completed installation, inspect completed raised access floor installation together with customer using manufacturers standard “completed inspection form” and sign off for approval. Provide one copy to the customer and return one copy to manufacturer as a proof of completion and acceptance.

- After receipt of “completed inspection form”, manufacturer shall provide customer with a detailed warranty document dated and signed by authorized officer of the manufacturer.

## INTERCOM SYSTEM

### General

- Fully digital, distributed network-based IP-intercom system (LAN/WAN). Easy setup/update/maintenance via PC software or Web browser with password.

- Connection of standard receivers from two-wire cable to the mediation unit or the IP stations across the network.

- Links allow quantization with a sampling rate of 16 kHz for a 16-bit a high-quality sound with a frequency range of 300 Hz to 7 kHz at full-duplex conversations. Hands-free calling is possible through ECHO suppression in this quality.

- Programmable intercom functions:

- Call, announcements, speed dial, manual call forwarding, automatic call forwarding, time-based call forwarding, adjustable time limitation for discussions, announcements and ringtone, manual activation of control outputs, automatic activation of control outputs (E.g. camera activation with reputation), automatic call activation control input, group call, call forwarding to "Busy", Office - call forward unconditional (time adjustable), auto answer, classic answer, automatic direct dial at the receiver, priority call, call Priority announcement priority, choice of up to 8 sources of background music, adjustable microphone sensitivity, Ringer volume, speaker volume.

- Distribution of stations in up to 160 zones. Call announcement up to 160 call zones / 1279 receivers at the same time possible. Grouping with customizable access rights regarding call and announcement permissions of the groups themselves.

- Ability to customize the bandwidth of a connection of 48.5 kbps up 130 kbps on the available network capacity.

- Automatic system diagnosis (every 20 seconds) of receivers, teaching units, IP Intercoms and universal interface for the network status, CPU errors, synchronization problem and missing receivers.

- Error signalling by freely programmable control output.

- Monitoring / system information via Web browser: Access / change network settings, monitor network status, status / action monitoring receivers, operational log (LOG), data stream Protocol (LOG), firmware update, reboot, change system name and password

- Possibility of recording conversations through establishment of a PC-based recording software.

- Remote control of receivers with a PC through a software setup.

- Depending on the system configuration, receivers, 1280 control inputs, 1280 control outputs, 160 audio inputs and 160 audio outputs can be operated up to 1280

### Audio Server

- Fully digital IP mediation unit with connections for 16 stations. Connection to other teaching units, universal interface and IP intercom stations on a network. Connecting the stations in 2-wire technique.

- No separate power supply of needed receivers. 1 internal and 2 external communication channels are also available.

Programmable functions:

- Call, announcements, speed dial, manual call forwarding, automatic call forwarding, time-based call routing, adjustable time limitation for discussions, announcements and ringtone, automatic activation of control outputs (E.g. call door intercom - CCTV via contact output activation), automatic call activation control input, group call, call forwarding to "Busy", Office - call forward unconditional (time adjustable), auto answer, classic answer, automatic direct dial at the receiver, priority call, choosing from up to 8 sources of background music, adjustable microphone sensitivity, ringer volume, speaker volume.

- Additional grouping with customizable access rights regarding call and announcement permissions of the groups themselves.

- 3 Status LED indicators for: operation, status, network.

### IP Desktop Master Station with Display & Handset

- Multifunctional master station with handset and speakerphone with ECHO compensator, LCD display with 16 characters, 2 lines, 8 programmable direct dial keys, connection for headset connection of external speaker, menu functions.

- 10 Buttons, 4 programmable speed dial buttons, 2 function keys, talk priority button, delete button, call button (for announcement), answer key (for announcement), hold-down button, transfer button (manual call forwarding), redial.

- Function call button for activation control output, call forwarding, Office transfer, time-based call forwarding, busy forwarding, background music.

- Programming the direct dial keys (follow)

- Indicator connected stations at mediation unit

- Update function of the operation log (log file), change the IP address, subnet mask, default gateway of the mediation unit with password protection. Setting the system clock, system restart.

### Sub-station IP with 1 Button

- IP door intercom for direct connection to the network, speakerphone with echo cancellation, call button, control output (E.g. the door opening), dust and water protection com. IP54, extended working temperature range.

## SECURITY FENCE PERIMETER LIGHTING

- Lamps used in the security fence perimeter lighting system shall be of the compact fluorescent type to ensure instant cold and hot re-strike.

- The security fence perimeter fence lighting system shall consist of a streetlight luminaire, equipped with two 26watt compact fluorescent lamps and mounted at a rake angle of 15 above the horizontal and at 6 metres above ground level on a GRP/galvanised steel pole positioned 2m inside the outer fence.

- The spacing shall be in such a way as to achieve an average initial illumination level of 5 lux and a minimum initial illumination level of 3 lux in the area of the fence line.

- The streetlight type luminaire circuit shall be controlled by a photoelectric cell.

## EARTHING SYSTEM

### Earth-termination Rods (Copper, 14.3 mm in diameter, 1.2m with clamp)

- General

To ensure compatibility of component parts of the earth rod assembly, the items to be supplied shall consist of earth rods and accessories which form a "total system" (but excluding connectors and earthing enhancing compounds). This will include an assessment of the safety, productivity, reliability and longterm performance of the items.

The design of the rod assembly (including couplings and driving points) shall be of such mechanical strength that they shall withstand the stresses and abrasions present during installation with an electric/pneumatic hammer.

The design of the rods and couplings shall be such that during installation, the connection between the rod and the coupling shall "self-tighten". This self-tightening shall have the effect of improving the electrical and mechanical performances of the rod/coupling combination.

The Tenderer shall state the design features of the rod and accessories which verify the following features:

- Self-tightening

- Improved electrical connection

- No damage to the copper sheath on installation.

The rod system shall be extendable by the use of appropriate couplings.

All items including rods, couplings, driving tips, driving caps and connectors shall be clean, free of burrs, cracks and sharp edges. The ends of the rods shall be chamfered.

Methods of covering the top of the earth rod at each earthing installation. The application of such a covering shall protect against corrosion of the earth rod. The covering does not have to meet any specific criteria eg. UV-stabilised.

Recommended procedure for the correct assembly of the various components of the earthing, system including the earth rod, coupling, driving mechanism, driving points and connectors.

- Rods – General

The earth rods shall have a nominal outside diameter of 13 mm and a nominal length of 150 mm. The rod shall consist of a steel core of minimum grade AS 3679.1-250.

The copper sheath shall be either molecularly bonded or extruded so as to maintain intimate contact with the steel core of the earth rod. The application of the copper sheath shall prevent any electrolytic action to be initiated by moisture ingress between the copper and the steel.

Tenderers shall state the method used to apply the copper sheath to the rod together with the design features to verify the prevention of moisture ingress.

Extruded sheath rods shall have a final minimum thickness of copper of 0.45 mm.

Rods which have the copper applied electrolytically, shall have a minimum copper thickness of 0.25 mm.

Rods shall be “tapered" type complying with the clauses described below.

NOTE: Threaded rods are NOT acceptable.

- Rods – Tapered

Both ends of the rods shall be tapered. The taper shall be approximately 3:100 on diameter and the length of taper shall be at least 50 mm long (as measured parallel to the axis of the earth rod).

- 5.4 Couplings

- The coupling device shall be designed to ensure good permanent electrical conductivity is maintained between the joined earth rods throughout a service life of 35 years for the installed earth rod assembly.

- The couplings shall be manufactured from material compatible with the rods. The material used shall be selected to ensure that electrolytic action and/or stress corrosion cracking will not occur. In addition, the surfaces of the couplings exposed to the soil, shall be corrosion resistant.

- 5.5 Driving Point

- The driving points shall be designed to reduce the driving effort on the earth rod. The driving point shall be designed to prevent damage to the copper sheath during the installation process.

- Both "Normal" and "Star" (rock) type driving points are required. The diameter of both types of driving points must NOT be LESS THAN the diameter of the earth rod/coupler assembly.

- Driving Mechanism (Head + Pin as applicable)

- The driving mechanism shall be used in conjunction with an electric/pneumatic hammer.

- The driving mechanism shall cover the rod sufficiently so as to prevent it from bouncing off the rod when used in conjunction with an electric/pneumatic hammer.

The driving head shall not damage the copper coating of the earth rod. Further, the driving mechanism shall not distort the coupling and/or rod to such an extent that an additional earth rod cannot be fitted into the coupling.

Full details concerning the method of installation including:

- The removability of the driving pin and/or the last coupling when the installation process is completed

- The requirement for a coupling for driving purposes.

The extent of re-useability of the driving pin and the coupling.

- Compression Connectors

- Connector(s) shall satisfy the following requirements:

- Be suitable for direct burial in the ground.

- Connect a 13 mm diameter rod with a stranded copper conductor of the following sizes :-

- Minimum conductor size: 50 mm² (19/1.78)

- Maximum conductor size: 70 mm² (19/2.14)

- Be used to join the following stranded copper conductors:

- 50 mm² to 50 mm²

- 50 mm2 to 70 mm²

- 70 mm² to 70 mm²

- The same method of connection shall be used for a conductor/conductor joint as well as a conductor/rod joint.

- The "C" shaped compression fitting is the preferred compression type connector.

- The design of the connector shall allow the laying of two cables side by side when making a

- Conductor / conductor connection.

- Some form of anti-oxidant grease covering the inside of the connector is required for compression type fittings.

- Indicate if the rod requires pre-crimping prior to compressing the connector.

- Bolted Connectors

- Connectors (Earth Rod/Conductor) shall satisfy the following requirements:

- Be suitable for direct burial in the ground.

- Be suitable for connecting a 13 mm diameter rod with one or two stranded copper conductors of the following sizes:

- Minimum conductor size: 35 mm²

- Maximum conductor size: 70 mm²

- Be of double saddle type that houses the conductor and earth rod separately.

- Be of materials which are resistant to corrosion and parts of the connector which are in direct contact with the conductor and earth rod shall be of material which does not cause interface corrosion.

- The Connectors (conductor/conductor) shall satisfy the following requirements:

- Be suitable for underground applications and shall have corrosion resistant properties similar to the 'earth rod/conductor' type connectors

- The Connectors (conductor /conductor) shall be suitable for joining the following types of stranded copper conductor;

- 35mm2 to 35 mm²

- 35mm2 to 70 mm²

- 70mm2 to 70 mm²

- The connectors shall be supplied with copper M10 nuts

- All bolts and washers shall be copper.

- All nuts shall be copper.

- Copper bolts and nuts shall be suitably greased to prevent binding

- Advise the minimum and maximum recommended tightening torques as well as the specified tightening technique/procedure.

- Technical Characteristics

- Tenderers shall provide detailed drawings for all items tendered.

- Performance and Testing

Connectors

- Connectors shall be installed in accordance with the manufacturer’s instructions.

- The complete test procedure is given below:

- The earth rod/connector/conductor combination shall be tested in still air. The locations of the connections for injecting the test current shall be positioned not less than twenty (20) times the diameter of the earth rod from the centre of the connector for all tests.

- Tests shall be carried out on the following connection combinations for both compression and bolted type connectors as detailed below:

- 70 mm² conductor to earth rod (Both types)

- 70 mm² cable conductor to 70 mm² cable conductor (Both

- A minimum average test current of 5 kA, 50 Hz for 1 second (I2t of 25 MA2/second) shall be used for each test.

- Visual inspection after the test shall ensure that there is no damage to the connector and there is no severe discolouration to the connector and surrounding areas. There should be no loosening of the connection between the cable and the rod or between the cable and the cable.

- Provide test reports that verify the requirements detailed above before the first deliveries are accepted.

- Documentary Evidence

Documentary evidence shall be provided concerning the level of quality system certification associated with the supplier and /or the manufacturer. This documentation shall include the Capability Statement associated with the Quality System Certification.

### EARTHING

- A continuous 70mm2, bare, stranded, copper earthing conductor shall be buried a minimum of 600 mm on the inside and run the continuous length of the perimeter.

- At each third fence post, via cad-weld connections, the earthing conductor shall attach to the 70mm2 ground ring.

- All doors of field cabinets shall be earthed.

- At a point nearest the main electronics equipment room, a 70mm2, bare, stranded, copper conductor shall bond the buildings electrical system ground bus to the 70mm2 ground ring

- All direct buried ground connections shall be cad-weld type connections.

## TRANSIENT VOLTAGE SURGE SUPPRESSION

This section describes the materials and installation requirements for Transient Voltage Surge Suppression (TVSS) devices, also known herein as Surge Protective Devices (SPD’s), for the protection of AC electrical circuits and electronic equipment from the effects of lightning induced transients, other externally generated transients, and internally generated transients.

- There are two types of surge arresters on low voltage AC systems – namely Class 1 and Class 2.

- The difference between them is their ability to divert energy in the form of a current.

- All metallic data, communications, video, and sensor lines entering or leaving a building shall be protected with surge protection devices.

- Earthing of protective devices shall be in accordance with the manufacturer's recommendations.

- All signal line protective devices shall be located at the terminal point nearest the cable interface with the exterior cable plant.

- Where equipment is fed from a panel board not protected by a panel board protector, provide a branch circuit protector installed at the panel board.

### Lightning Protection - Class 1 high energy Metal Oxide Varistor (MOV)

- Can divert energy with a current wave form of 10/350µs – the rise time is 10µs and the tail of wave is 350µs to 50%

- Typical current ratings 10Ka to 35Ka – 10/350µs wave form.

- Location of use: main distribution boards.

### Surge Suppression - Class 2 Silicon Avalanche Diode (SAD)

- Diverts energy with a wave form of 8/20µs – the rise time is 8µs and the tail of wave is 350µs to 50%

- Typical current ratings 5Ka to 200 Ka – 8/20µs wave form.

- Location of use: Sub-distribution boards or as close as possible to a protected device.

# TECHNICAL SPECIFICATIONS FOR INTEGRATED SECURITY SYSTEMS

## ACCESS CONTROL SYSTEM

### Fingerprint Processing Unit – Take-ons

- Fingerprint sensor:		Single fingerprint optical sensor

500 dpi resolution, 256 grey levels

(23mm x 23 mm) acquisition area

- Authentication:		< 0.7 sec

- Identification:		< 0.9 sec in 1:1000 mode

- Internal database:		From 500 to 5000 users

- template & image formats:	ISO 19794-2, ANSI/INCITS 378

ISO 19794-4, WSQ compressed image

- Interface:			USB

### Fingerprint reader: Indoor (Type 1)

- CPU: 				ARM Cortex-A9 core 1GHz

- Contactless reader options: 	Prox, iClass, MIFARE/MIFARE Plus/DESFire/NFC

- Network/Communication:	Ethernet, RS485, USB

Wi-Fi option

- Power supply:		12V-24V DC, Power over Ethernet (PoE)

- Up to 10,000 users (30,000 templates) in 1:N identification mode

- 1:10,000 user matching in 1 second

- Up to 250,000 users in 1:1 verification mode

- Inputs/outputs: Wiegand In & Out (customizable up to 512 bits), Door Relay, 2 General Purpose Inputs (including Door monitoring), 2 General Purpose Outputs

- Tamper switches

- Internal storage capacity:	512MB Flash, 512MB RAM

- 1:N mode: 3,000 user records, extendable to 10,000 with license (3 templates each, including 1 duress)

- 1:1 mode: 250,000 user IDs

- 1 Million transaction logs

- Anti-fraud features:	 	Fake finger detection

Duress finger

Timed anti-pass back function

Banned/authorized user lists

- Operating temperature:	-20° to +55°C

- Humidity: 			10% to 80% (non-condensing)

- Ingress protection: 		IP65

- Mechanical impact protection: IK08

### Fingerprint reader: Indoor (Type 2)

- CPU:					ARM Cortex-A9 core 1GHz

5” WVGA color Touchscreen, VGA Camera

- Contactless reader options:		Prox, iClass, MIFARE/MIFARE Plus/DESFire

- Network/Communication:		Ethernet, RS485, RS422, USB Wi-Fi and 3G options

- Internal storage capacity:		512MB Flash, 512MB RAM +, 8GB microSD Card

5000 user records (2 fingers + 					1 duress each), extendable up to 100 000 with licenses

250,000 IDs in authorized user list

1 Million transaction logs

10,000 face picture logs

- Inputs/outputs: 			Wiegand In & Out (customizable up to 512 bits),

Door Relay, 3 GPI (including Door monitoring), 3 GPO

- Operating temperature: 		-20° to +60°C

- Humidity: 				10% to 80% (non-condensing)

- Ingress Protection: 			IP65

- Power supply: 			12V-24V DC

Power over Ethernet (PoE)

- Tamper switches

### Fingerprint reader: Outdoor

- CPU: 					ARM Cortex-A9 core 1GHz

5” WVGA color capacitive touchscreen with ambient light sensor

- Contactless reader options:		Prox, iClass, MIFARE/MIFARE Plus/DESFire

- Internal storage capacity: 		512MB Flash, 1GB RAM + 8GB microSD Card

5000 user records (2 fingers + 1 duress each), extendable up to 100,000 with licenses

250,000 IDs in authorized user list

1 Million transaction logs

10,000 face picture logs

- Network/Communication:		Ethernet, RS485, RS422, USB

Wi-Fi option

- Inputs/outputs:			Wiegand In & Out (customizable up to 512 bits), Door Relay, 3

GPI (including Door monitoring), 3 GPO

- Operating temperature: 		-20° to +60°C

- Relative humidity: 			10 to 95% (non-condensing)

- Power supply:			12 to 24 V DC (1A min @12V)

Power over Ethernet (PoE)

- Tamper switches

- Ingress protection: 			IP65

- Mechanical impact protection: 	IK09

### Multi-function Single-door Controllers with backup batteries (local product)

- Input Voltage:			10 V DC to 30 V DC, polarity sensitive.

- Power Requirements:		Current (mA)		Power (W)

12 V DC with no peripherals:

connected and relays off			75			0.90

24 V DC with no peripherals

connected and relays off:		40			0.96

- System Battery:			Battery Type:		12 V 7 Ahr (Max) Sealed Lead Acid Battery.

- Real Time Clock (RTC) Backup Battery:	Battery Type:	1 x 3 V, CR2032, Lithium perimeter Battery.

Battery Life:	1 Year with Power OFF, 5 years with Power ON

- Ethernet Port:		Standard Ethernet RJ45 connector.

- RS485 Terminal Port:	Electrical Interface:	RS485.

Baud Rate:		38 400.

Data Format:		8 data bits, no parity, 1 stop bit.

Communications Protocol: Secure Communications Protocol.

- Operating Temperature:	-25°C to +60°C

- Humidity Range:		0 to 95% relative humidity at +40°C

- Reader Options:		Power Output:	12 V DC and 5 V DC (selectable) at maximum 200 mA.

Baud Rate:	9 600.

Data Format:	8 data bits, no parity, 1 stop bit.

- Digital Inputs:		Input Type:	4 Dry-contact inputs.

- Relays:			Relay Output:	2 Relays, Form C, each with NO, COM and NC contacts.

- Operations:			100 000 Minimum

### System / Network / Master Controllers

- Operating:		 	-10°C to +50°C

- Humidity Range: 		0 to 95% relative humidity at +40°C noncondensing

- IP Rating: 			IP30.

- Power Requirements:	Input Voltage: 10V DC to 30V DC.

Current (mA) 	Power (W)

Supply Voltage 10V DC:	420 			4.2

Supply Voltage 30V DC:	140 			4.2

- Power Input Protection: 	Reverse polarity on DC power inputs, over-voltage and

over-current protection are provided on the Controller.

- Ethernet Port:		Connection: Standard Ethernet RJ45 connector.

10/100 Mbps, half or full duplex.

Protocol: TCP/IP, UDP

- RS485 1 (Controller) Port:	Baud Rates: 9 600, 19 200, 28 800, 38 400 and 57 600 selectable

via the Communications Protocol.

Data Format: 8 data bits, no parity, 1 stop bit.

- RS485 2 (Terminal) Port:	Baud Rates: 9 600, 19 200, 28 800, 38 400, 57 600 and 76 800

selectable via the Protocol.

Data Format: 8 data bits, no parity, 1 stop bit.

- Memory:			RAM (Non-volatile) : 64 MBytes.

Flash ROM : 8 MBytes.

- Real Time Clock (RTC)

Backup Battery:	Battery Type: 1 x 3 V, CR2032, Lithium perimeter Battery.

Battery Life: 5 Years (with power OFF).

- System Battery:		Battery Type: 6 V 3 Ahr Sealed Lead Acid Battery.

Battery Life: 4-6 Hours uninterrupted operation.

48 Hours Power Shutdown (Hibernation Mode).

- Anti-tamper Protection:	2 Internal switches.

- Test Modes:			Power-on Self-test: RAM, Flash-ROM, RTC.

- Diagnostic LED Indicators:	Power-on LED: Red LED (internally visible).

Incoming RS485 1 (Controller): Flashing Green LED (internally visible).

Outgoing RS485 1 (Controller): Flashing Red LED (internally visible).

Incoming RS485 2 (Terminal): Flashing Green LED (internally visible).

Outgoing RS485 2 (Terminal): Flashing Red LED (internally visible).

Link Speed LED (Ethernet): Flashing Red LED (internally visible).

Duplex Mode LED (Ethernet): Flashing Red LED (internally visible).

Link Active LED (Ethernet): Flashing Red LED (internally visible).

CPU Usage: Red LED (internally visible).

On = Idle, Off = Busy.

CPU Running: Red LED (internally visible).

On = Yes, Off = No.

CPU Fault: Red LED (internally visible).

On = Fault Condition, Off = Ok.

### Electromagnetic locks

- 300KG Mortice mount

- Slim-line, Mortise Mount type.

- Handle a minimum force of 3000N (300Kg).

- Input voltage 12/24VDC.

- Current drawn between 250mA and 500mA.

- Finish – Anodized Aluminium.

- Typical dimensions: 230 (L) x 40 (W) x 25 mm (D).

- Monitoring – relay.

- All bolts and nuts used for this installation shall be tamperproof. None of these bolts must be visible from secured side of the door.

- The magnetic lock shall furthermore be installed in such a way that no wires of the magnetic lock are visible.

- 300KG standard surface mount

Slim-line, standard surface mount type.

- Handle a minimum force of 3000N (300Kg).

- Input voltage 12/24VDC.

- Current drawn between 250mA and 500mA.

- Finish – Anodized Aluminium.

- Typical dimensions: 270 x 50 x 25 mm.

- Monitoring – relay.

- All bolts and nuts used for this installation shall be tamperproof. None of these bolts must be visible form secured side of the door.

- The magnetic lock shall furthermore be installed in such a way that no wires of the magnetic lock are visible.

### Electromechanical locks

- Exterior doors

- Operating Voltage:			12-24 VDC (-10%/+15%)

- Current consumption:		max 550 mA (12 VDC)

max 270 mA (24 VDC)

idle 240 mA (12 VDC)

max 270 mA (24 VDC)

idle 110mA (24 VDC)

- Monitoring:				Microswitch 0.4A 30V AC

(deadlock status)

- Operational temperature range:	-20°C to +60°C

- Case/Cover:				High Purity zinc alloy

- Forend:				25mm

- Adjustable Backset:			25, 30, 35mm

- Latchbolts:				Bolt throw 14.5mm

- Door Clearance:			3-5 mm

- Cylinder:				ABLOY classic or ABLOY Disklock Pro

- Cabling Recommended cable: 	0.82mm2 cable runs up to 30m

- Standard Finishes:			Chrome plated forend, lock case yellow chrome plated

- Interior doors

- Voltage:				12-24 Vdc -10%/ +15% STAB

- Current:				550mA (max) 240mA holding @12Vdc

270mA (max) 110mA holding @24Vdc

- Monitoring:				Microswitch 0.4A 30V AC

(deadlock status)

- Operational temperature range:	-20°C to +60°C

- Case/Cover:				High Purity zinc alloy

- Forend:				25mm

- Backset:				25, 28, 30, 33, 35mm (adjustable)

- Latchbolts:				Double action latch 14.5mm

- Door Clearance:			3-5 mm

- Cylinder:				ABLOY classic or ABLOY Disklock Pro

- Cabling Recommended cable: 	0.82mm2 cable runs up to 30m

- Standard Finishes:			Chrome plated forend, lock case yellow chrome plated

- Double Cylinder

CONSTRUCTION

- Cylinder housing:		Brass outside cylinder housing of case-hardened steel

- Cylinder plug:		Brass

- Discs and washers:		Tin bronze

- Number of discs:		11

### Heavy duty door closer

- Adjustable spring size 1–4.

- The closer must allow for disabled persons and be adjustable to meet 4 kg maximum opening force requirements for exterior doors.

- Compact closer body and cement case maximum 50mm deep suited for thin slab concrete construction.

- Accommodates doors weighing up to 120 kg and measuring up to 1080 mm wide interior and 910 mm exterior.

- Shall handle mechanical back check of approximately 70°.

- Dual thermostatic control valves combined with special hydraulic fluid provide controlled closing from 175°.

- Have a pressure relief valve protects closer from damage caused by forced closing.

- Closer adjustment in cement case provides 10mm lateral,

- 6 mm longitudinal, and 4mm height adjustment.

- Shall have optional sealing compound SC-1 to prevent water or cleaning solvent from entering the cement case.

- Valve adjustment 15º– 0º.

- Valve adjustment 175º–15º.

- Mechanical back check at approximately 70º.

- Single point hold open units available at 90º and 105º.

### Green break glass

- The break glass shall be able to switch 50VAC or 30 VDC @ 8A.

- The break glass shall be able to switch 50VDC @ 3A.

- Environmental Conditions:

- Temperature Range: -40°C – +85°C.

- Relative Humidity: 0 – 90% Non-Condensing Relative Humidity.

- The break glass shall be operable with a glass lens or a resettable lens.

- The break glass shall have surface and flush mounting options.

- The break glass shall have a high quality micro switch.

- The break glass shall have the standard EN54 symbols on it.

- Accept hinged cover as a standard.

- The break glass shall have a built in key test site.

- Break glass units shall be in accordance with BS 5839-2.

- The unit shall be large enough to cover 65 mm o/ conduit draw box when the unit is surface mounted.

- Flush mounted units shall be provided with a special flush mounting box, which can accept electrical conduit terminations.

- Surface mounted units shall be deep enough to terminate 20 mm ø conduits into the unit, and shall be mounted solidly on the wall by means of their back plates.

- The wiring terminals of the unit shall be able to accept wiring lugs, and shall be of the screw and clamp plate type to hold a lug firmly pressed against its contact surface. Spring loaded push-in contacts will not be acceptable.

- The glass shall not be damaged when it is pressed.

- The glass shall be resettable with a standard break glass key.

- The glass shall be marked with the standard EN54 symbols and/or a “PRESS HERE” indication.

### Door position switch/door status monitor (Recessed)

- Operating gap (minimum) 10 mm.

- Connection via 4 wires.

- Contact type must be NC or NO.

- Typical Dimensions Ø22 x 40 mm to Ø26 x 40 mm.

- Colour: White.

- Minimum Contact switching rating: 100V @ 0.5A.

- Environmental Conditions:

- Operating Temperature Range: -40 to +65º C.

- Relative Humidity: 5 – 95 % Non-Condensing.

### Overhead Mounted Magnetic Switches

- Contact Rating:				10W/VA

- Switching Voltage (Max.):			200 VDC

- Switching Current (Max.):			0.5 Amp.

- Contact Resistance (Min.):			150 milli ohms

- Life Expectancy:				10x 10 6 Operations

- Insulation Resistance:				10 9 ohms

- Shock Resistance:				30G for 11mSec.

- Vibration Resistance:			20G ( 10 to 1000Hz)

- Armour Jacket:				Stainless Steel (Type 304)

- Ideal for use on metal doors

### Roller Shutter Door Contacts

- Contact type:				3 Single-pole NO contact

- Operating distance:		 	34mm +/- 5mm

- Power input Max:		 	40V DC

- Switching current Max:	 	500mA

- Contact capacity Max:	 	6W

- Transition resistance Max:		0,15 W

- Breakdown voltage:			 >250 V

- Connecting cable:			 4 x 0,14 mm² Cu tinned, suitable for LSA technique

- Outer cable colour:			Grey

- Inner conductor:			Blue, green, yellow, red

- Cable dimension:			Ø 3,2mm

- Metal hose:				L 1 m, ⌀6 x 9 mm steel galvanized, PVC coated

- Magnet:				Ø 12 x 55mm AlNiCo 5, axial polarized

- Housing colour:			grey

- Temperature range:			-40°C to +70°C

- Ingress Protection:			IP67

### Override key switch

- Three (3) high security keys, with key certificates.

- Electrical Contacts:

- Double Change-Over Contact.

- Minimum Contact Rating: 100V @ 0.5A.

- Mounting Accessories.

### Reports Printers.

- Print speed:				Black:		Up to 17 ppm

Color: 		Up to 4 ppm

- Print technology:			Laser

- Print resolution technologies:	600 x 600

- Print cartridges number:		4 (1 each black, cyan, yellow, magenta), 1 imaging drum

- Printer management:		Windows: Device Toolbox, Status Alerts (default install); Mac: Utility

- Scan type:				Flatbed, ADF

- Print speed:				Up to 7.5 ipm (b&w), up to 5.5 ipm (color)

- Scan resolution Enhanced: 		Up to 1200 dpi; Hardware: Up to 1200 x 1200 dpi; Optical: Up to 1200

- Scan technology:			Contact Image Sensor (CIS)

- Scan file format:			Windows Scan SW supports file format: JPG, RAW(BMP), PDF, TIFF, PNG; Mac Scan SW supports file format: TIFF, PNG, JPEG, JPEG-2000, PDF, PDF Searchable, RTF, TXT

- Bit depth/Grayscale Levels:		24-bit/256

- Standard connectivity:		Hi-Speed USB 2.0 port; built-in Fast Ethernet 10/100Base-TX network port; Wireless

- Network capabilities:		Via built-in 10/100Base-T TCP/IP networking

- Network Ready:			Standard (built-in Fast Ethernet, WiFi 802.11 b/g/n)

- Wireless capability:			Yes, built-in WiFi 802.11b/g/n, WPA/WPA2

- Modem:				33.6 kbps

- Memory:				128 MB

- Processor speed:			600 MHz

- Duty cycle (monthly):		Up to 20,000 pages

- Control panel:			3.0 in 960 x 240 pixel backlit graphical display; touchscreen; buttons (Home, Cancel, Help, Right/Left Arrows, Back); LED indicator lights (Ready, Error, Wireless)

- Display:				3.0-in LCD (color graphics)

- Power supply required: 		Input voltage: 220VAC (+/- 10%), 50 Hz

- Power consumption:			290 watts

- Operating: 				15°C to 30°C

- Relative Humidity:			20 – 80% RH

### Webcam

- Basic requirements

- 1 GHz

- 512 MB RAM or more

- 200 MB hard drive space

- Internet connection

- USB 1.1 port (2.0 recommended)

- For HD 720p video calling and Full HD 1080p video recording:

- 2.4 GHz Intel® Core™2 Duo

- 2 GB RAM

- 200 MB hard drive space

- USB 2.0 port

- 1 Mbps upload speed or higher

- 1280 x 720 screen resolution

- Technical Specifications

- Full HD 1080p video capture (up to 1920 x 1080 pixels) with recommended system

- HD video calling (1280 x 720 pixels) with recommended system

- Logitech Fluid Crystal™ Technology*

- Autofocus

- Photos: Up to 8 megapixels (software enhanced)

- Built-in mics with automatic noise reduction

- Hi-Speed USB 2.0 certified (recommended)

- Universal clip fits laptops, LCD or CRT monitors

### Programmable Logic Controllers

- Processor:				Intel® Atom™ Z510, 1.1 GHz or equivalent

- Flash memory:			64 MB

- Main memory:			512 MB RAM

- Interfaces:				2 x RJ 45, 10/100/1000 Mbit/s, DVI-D, 2 x USB 2.0

- Diagnostics LED:			1 x power, 1 x TC status, 2 x bus status

- Clock:					Internal battery-backed

- Operating system:			Embedded Linux, Windows CE or Windows Embedded Standard

- Power supply:			15-30 V DC

- Dielectric strength:			500 V (supply/internal electronics)

- I/O Current:				1A

- Operating Temperature:		-15°C to +60°C

- Relative Humidity:			95 %, no condensation

### Door Control Modules

- Interfaces:				2 x RJ 45 Ethernet, 10/100 Mbit/s (Autosensing)

- Diagnostics LED:			1 x Power, 1 x TC status, 2 x Bus Status

- Operating system:			Embedded Linux, Windows CE or Windows Embedded Standard

- Power supply:			15-30 V DC

- Dielectric strength:			500 V (supply/internal electronics)

- I/O Current:				500 mA

- Operating Temperature:		-15 to +60 °C

- Relative humidity:			95 %, no condensation

- Digital Inputs:			8

- Digital Outputs:			4

### Control Modules

- Interfaces:				2 x RJ 45 Ethernet, 10/100 Mbit/s (Autosensing)

- Diagnostics LED:			1 x power, 1 x TC status, 2 x bus status

- Operating system:			Embedded Linux, Windows CE or Windows Embedded Standard

- Power supply:			15-30 V DC

- Dielectric strength:			500 V (supply/internal electronics)

- I/O Current:				500 mA

- Operating Temperature:		-15 to +60 °C

- Relative humidity:			95 %, no condensation

- Digital Inputs:			16

- Digital Outputs:			16

## ALARM SYSTEM

2.2.1. Zones Control Panel Expandable to 40 zones

- Zones:							8-40

- Zone expansion (Star, Bus or Wireless):		32

- Number of expansion buses:			1

- Partitions/Areas:					4

- Groups per partition:				4

- User Codes:						60

- Programmable Outputs:				6-38

- Output Expansion Modules:			4

- Supervised Power Supplies:				8

- Digital Key Readers:					16

- Keypads:						12

- Account numbers:					8

- Weekly time schedules:				16

- Event Log:						250 to 512

- Main Power:						16.5VAC - 25VAC transformer from 220V AC

- Auxiliary Power:					12V DC - 1.5A

- Battery - maximum allocatable:			12V DC - 17 AH

- Programmable outputs on main board:		6 - one 3A relay, one 500mA open collector and four 70 mA O.C.

- Operating Temperature:				0ºC-55ºC

    - 8 Zone wired bus expander module

- Switched auxiliary power output

- 22 Programmable zone types

- Programmable loop response for each zone from 10ms to 4 hours

- Zone termination - N/C, N/O, end-of-line resistor and double end-of-line resistor

    - Outdoor Dual Technology Detectors

- Detection method:					Two microwave and Two, PIR channels

- Wide angle coverage:				15m 90º

- Long-range coverage:				23m 5º

- Barrier coverage:					15m 5º

- Mounting height:					1m to 2.7m

- Pet immunity:					Animals up to 70cm head height with no weight limitation

- Anti-mask and dirty lens indications:		Via 4 active IR channels

- Operating voltage:					9-16 VDC

- Current consumption Relay mode at 12V:		45mA typical, 70mA maximum

- Current consumption bus mode at 12V:		30mA typical, 55mA maximum

- Alarm contact:					NC, 100mA, 24 VDC

- Tamper contact:					NC, 100mA, 24 VDC

- Anti-mask contact:					NC, 100mA, 24 VDC

- Dirty lens output:					70mA open collector

- RF immunity:					40V/m from 30MHz to 2 GHz

- Environment rating:					IP 65

- Operating temperature:				-30ºC to 60ºC

    - Indoor Dual Technology Detectors

- Pet Immunity:				Yes

- Current Consumption:			12mA

- Alarm Contacts:				NC, 100mA, 24VDC maximum

- Tamper Contacts:				NC, 100mA, 24VDC maximum

- Alarm Time:					2,2 seconds, minimum

- Adjustable Pulse Count:			1,2,3

- Temperature Compensation:		Automatic, thermistor controlled

- Swivel adjustment:				Horizontal: ±25° Vertical: +5°,-20°

- Optical filtering:				White light protection, pigmented lens

- RF Immunity:				(10MHz to 1GHz)

- Operating Temperature:			-10°C to 50°C

    - Dual Technology Detectors (360 deg)

- Detection technologies:		Dual element PIR + Microwave

- Operating voltage: 			9 to 16VDC

- Current consumption:		15mA at 12V

- Alarm contacts: 			100mA, 24V, N.C.

- Tamper contacts: 			100mA, 24V, N.C.

- PIR lens coverage: 			110º angle, 360º overview

- Detection zones 60: 			30 Fresnel facets arranged in 3 optical levels; 12 external, 12 middle and 6 internal facets

- Optical filtering: 			White light protection

- Selectable pulse count:		1,2 (alternate polarity)

- Temperature compensation:	Microprocessor controlled

- RF immunity: 			30V/m from 10MHz to 1GHz

- Walk Test:				Display 3 LEDs

- Operating temperature: 		0ºC to 55ºC

- Installation Height: 			Up to 4m

    - Fixed Word LCD Keypad

- Low profile touchscreen keypads with proximity available in black or white

- Intuitive menu-driven user interface

- Proximity Key Readers for easy arm/disarm operation

- Program Transfer Module for program backup and copying

    - LED Keypad

- LCD Viewable Area:				99 mm x 24 mm

- Current Draw:				125 mA (Max)

- Voltage:					12 VDC Nominal

- Operating Environment:			0° to 49°C

- Relative Humidity:				5% to 93%

    - VHF Transmitter

- Frequency Range:				132 - 174 MHz

- Channel Spacing:				12.5 KHz

- Operating Voltage:				10.5 to 13.8 Volts DC

- Modulation Method:				FM

- Frequency tolerance:			5 ppm

- Narrow Bandwidth Spurious Emissions:	a) Harmonic		> 60 dB

b) Non-harmonic	> 70 dB

- Deviation:					Adjustable between 1.5 and 2.5 KHz

Nominal		Approximately 2 KHz

Temperature range	-10 to + 60 C

Class of Emission	F3E

Antenna Impedance	50 Ohms

- Current Consumption:			Standby		30 mA

Transmit		1.8 Amps at 12V nominal

- Antenna Socket:				Internal tamper proof antenna connection

- Transmission Duration:			90 - 360 mS

- Telemetry Inputs:				Output voltage range

Positive Trip - 10.8~14V

Negative Trip - Open Collector 0~0.5V

The transmitter inputs accommodate only the

above alarm panel output voltage ranges.

Alarm panels which do not meet this requirement

will require a level converter interface.

- Reports a 4-digit code number, customer ID and 2hardwired telemetry conditions:

      - panic

      - alarm

      - TIP

      - RING

- Contact ID interface support:

- Up to 4 partitions are supported / reported

- Up to 31 zones reported

- (zone 32 reserved for universal or unknown zone)

- Up to 15 users / key holders reported

- (user 16 reserved for universal or unknown user)

    - Seismic/Safe detector

- Current Draw:				16 mA (Max)

- Sensitivity Setting:				Dual Stage Potentiometer

- Latching/Non-Latching:			(SS-101) 1st + Subsequent or Any (SS-102) 1st + Subsequent or Any + 6 Wire

- Indicator:					Two Color LED

- Relay Contact Rating:			150 mA, 24 V Resistive, 10 Ohm 1/4 Watt

- Time Relay Open In Alarm:		1 Second (Min)

- Operating Environment:			-20° to 60° C

- Relative Humidity:				0% to 90%

- Min sound Pressure Level: 			15 mA

- Operating Voltage: 				9 – 15 VDC

- Alarm Output: 				28 VDC, 500 mA

- Tamper Protection: 				Dual tamper alarm for cover and base plate

- Low-voltage Alarm: 				Voltage drops below 7.5 V

- Up to 3-meter range, sensitivity adjustments, UL & CE approved

    - Door Contacts - Flush mounted

- Contact Rating:				10W/VA

- Switching Voltage (Max.):			200 VDC

- Switching Current (Max.):			0.5 Amp.

- Contact Resistance (Min.):			150 milli ohms

- Life Expectancy:				10 x 106 Operations

- Insulation Resistance:			10 9 ohms

- Shock Resistance:				30G for 11mSec.

- Vibration Resistance:			20G (10 to 1000Hz)

- Armour Jacket:				Stainless Steel (Type 304)

    - Fixed Panic Transmitter Panic Buttons

| Electrical Rating: | 230 VDC, 4 Amp. |
| --- | --- |
| Operating temperature: | -20degree C to +80 degree C |
| Switching current: | 1.25A |
| Product type: | Panic Switch |

- Emergency Button:		Glows in the dark

- Operating voltage: 		12VDC

    - Wireless detector receiver module for remote arm / disarm functions

- Description

- Up to 128 users

- Full user identification

- Programmable form the keypad

- 2 relay outputs with 1A contacts

- More receivers for more partition control

- Excellent remote range

- Communicates with the Alarm Panel via a keypad bus

- Secure code hopping functionality

- The receiver can learn most rolling code transmitters

- Remote buttons can be programmed to arm/disarm; stay arm, panic, relay1, relay2, or no action

- 3 Second any button panic option

- Receiver shall have two outputs ideal for gate/garage or light control

- Dedicated tamper zone

    - 1,2, 4 & 6-Button Remote Transmitters

- Description

- Code-Hopping Encryption

- Unique antenna design incorporating the Keyring increases operating range by 50%

- Crystal frequency-controlled within +/- 100KHz

- Frequencies available are 403.55MHz and 433.92MHz

- 12V Battery operation - GP23A Alkaline Cell

- Typically 2 years battery life expected under normal use

- LED flashes when there is a low battery condition

- Rubber buttons are easy to press and click positively

    - 15Watt, 12V Outdoor Siren

- Key features

- 2 Tones: Steady or Yelp

- High Impact ABS Plastic

- Weather Resistant

- IP65 outdoor siren

- 108 dB @12V

- 600mA @ 12VDC

## CCTV SYSTEM

### Video Management Server / Recorder (Type 1)

- Processor:			Intel i3-2120 processor

- Socket:			1 x (Intel processor socket LGA1155)

- Chipset:			Intel Core logic chipset PCH Cougar Point C206

- Memory type:		DDR3 1066/1333 MHz UDIMM

- Max front side bus:		1333 MHz

- Memory installed:		4 GB, DDR3‑1333 SO‑DIMM (2 x 2 GB)

- Storage type:			4 trays: 3.5‑inch SATA

- Hard drives installed:	4 x HDD (2 TB 5400RPM GP) max

- Graphics:			1 x USB DVI port, onboard graphics VGA port

- Network:			1 x 1 GbE RJ45 port

- Power supply:		220 W (220 VAC)

- Power consumption:		(w/o hard drives) 82W max, 41W idle

- Power consumption:		(4 hard drives operating) 114W

- Form factor:			4‑bay mini tower

- Power supply:		1 x internal power supply

- USB ports:			4 x USB 2.0, 1 x USB 3.0 port

- Network:			1 x Gigabit Ethernet LAN

- Operating temperature:	+10 °C to +35 °C

- Operating relative humidity:8 to 90% (non-condensing)

- Storage capacity:		Up to 8TB

- All-in-one recording, viewing and management solution for network surveillance systems of up to 32

channels (all channels pre-licensed).

### Video Management Server / Recorder (Type 2)

- Processor:			Intel Xeon Quad Core X3430 (2.4 GHz, 8 M Cache, 95 W)

- Cache memory:		1 x 8 MB Level 2 cache

- Memory protection:		ECC unbuffered

- Max front side bus:		1333 MHz

- Memory installed:		4 GB, DDR3-1333 ECC UNB (2 x 2 GB)

- Storage type:			8 Trays: 3.5-inch SATA

- Hard drives installed:	DIP-7082-8HD: 16 TB, 2 TB SATA/300 7.200 RPM 3.5“

DIP-7083-8HD: 24 TB, 3 TB SATA/300 7.200 RPM 3.5“

- SAS RAID card:		2108 based SAS/SATA RAID card –

8 internal ports/low profile‑PCI‑E

- Graphics:			AMD FirePro V3900 1 GB, low profile

- Sound card:			Creative Sound Blaster PCI sound card

- OS drive:			Intel SSD 320 OVR, 80 GB (MLC)

- DVD writer:			Internal

- USB Ports:			4 USB 2.0

- Network:			Dual Intel 82574L Gigabit LAN

- Power Supply:		740W Platinum Level Redundant

- System AC input VA requirement:	309.71 VA

- Power consumption (fully populated):	373 W

- Operating Temperature:		+10 °C to +35 °C

- Operating Relative Humidity:	8 to 90% (non-condensing

- Storage capacity:			Up to 24TB

- RAID-5 hardware redundancy

- All-in-one recording, viewing and management solution for network surveillance systems of up to 128 channels (with 32 channels pre-licensed).

### Video Management Server / Recorder (Type 3)

- Processor:			Intel Xeon Processor E3-1275 V3 (8 MB Cache, 3.5 GHz)

- Cache memory:		8 MB Intel Smart Cache

- Memory protection:		ECC unbuffered

- Max front side bus:		1600 MHz

- Memory installed:		8 GB, DDR3-1666 ECC UNB (1 x 8 GB)

- Storage type:			8 Trays: 3.5-inch SATA

- Hard drives installed:	Data:	SATA-3, 7200 RPM, 64 MB, 3.5“, RAID-5

configuration

DIP-7183-4HD: 4 x 3 TB

DIP-7183-8HD: 8 x 3 TB

DIP-7184-4HD: 4 x 4 TB

DIP-7184-8HD: 8 x 4 TB

DIP-7186-8HD: 8 x 6 TB

DIP-7188-8HD: 8 x 8 TB

DIP-7180-00N: w/o HDD

OS:	2 x 120 GB SSD RAID-1 configuration

- SAS RAID card:		8 ports LSI 3108 SAS3 controller

- Graphics:			AMD FirePro W4100; 4 x Mini Display Port

- Sound card:			5.1 Channel 24-bit

- DVD writer:			Internal

- USB Ports:			Front: 2 USB 2.0 ports

Rear: 2 USB 2.0 ports, 2 USB 3.0 ports

- Network:			Dual Intel i210AT Gigabit LAN (teamed)

1 IPMI BMC port

- Form Factor:			2HU rack mount

- Power Supply:		740W Platinum Level Redundant

- System AC input VA requirement:	338.7VA

- Power consumption:		325.1 W

- Operating Temperature:		+10 °C to +35 °C

- Operating Relative Humidity:	8 to 90% (non-condensing

- Storage capacity:			Up to 64TB

- RAID-5 hardware redundancy

- All-in-one recording, viewing and management solution for network surveillance systems of up to 128 channels (with 32 channels pre-licensed).

### Video Management Server / Recorder (Type 4)

- Processor:			Intel Xeon Processor E3-1275 V3 (8 MB Cache, 3.5 GHz)

- Cache memory:		8 MB Intel Smart Cache

- Memory protection:		ECC unbuffered

- Max front side bus:		1600 MHz

- Memory installed:		8 GB, DDR3-1666 ECC UNB (1 x 8 GB)

- Storage type:			16 Trays: 3.5-inch SATA

- Hard drives installed:	Data:	SATA-3, 7200 RPM, 64 MB, 3.5“, RAID-5

configuration

DIP-71F3-16HD: 16 x 3 TB

DIP-71F4-16HD: 16 x 4 TB

DIP-71F6-16HD: 16 x 6 TB

DIP-71F8-16HD: 16 x 8 TB

DIP-71F0-00N: w/o HDD

OS:	2 x 120 GB SSD RAID-1 configuration

- SAS RAID card:		8 ports LSI 3108 SAS3 controller

- Graphics:			AMD FirePro W4100; 4 x Mini Display Port

- Sound card:			5.1 Channel 24-bit

- DVD writer:			Internal

- USB Ports:			Front: 2 USB 2.0 ports

Rear: 2 USB 2.0 ports, 2 USB 3.0 ports

- Network:			Dual Intel i210AT Gigabit LAN (teamed)

1 IPMI BMC port

- Form Factor:			3HU rack mount

- Power Supply:		1200 W Platinum Level Redundant

- System AC input VA requirement:	458.6 VA

- Power consumption:		440.3 W

- Operating Temperature:		+10 °C to +35 °C

- Operating Relative Humidity:	8 to 90% (non-condensing

- Storage capacity:			Up to 128TB

- RAID-5 hardware redundancy

- All-in-one recording, viewing and management solution for network surveillance systems of up to 128 channels (with 32 channels pre-licensed).

### Network Video Recorder (Type 1)

- Processor:			Intel Atom D525 processor + Intel ICH 9R storage controller

- Chipset			Intel 82801IR I/O controller hub (ICH 9R) (Southbridge)

- Memory type:		DDR3 SO‑DIMM

- Max front side bus:		1333 MHz

- Memory installed:		4 GB, DDR3‑1333 SO‑DIMM (2 x 2 GB)

- Storage type:			4 trays: 3.5‑inch SATA

- Hard drives installed:	4 x HDD (2 TB 5400RPM GP) max

- Network:			1 x 1 GbE RJ45 port

- Power supply:		220 W (220 VAC)

- Power consumption:		(4 hard drives operating) 114W

- USB ports:			3 x USB 2.0, 2 x USB 3.0 port

- Network:			1 x Gigabit Ethernet LAN

- Operating temperature:	+10 °C to +35 °C

- Operating relative humidity:8 to 90% (non-condensing)

- Storage capacity:		Up to 8TB

- Fully featured video recording solution for up to 16 channels

### Network Video Recorder (Type 2)

- Processor:			Intel N3150

- Storage controller		Marvell 88SE9215

- Memory type:		DDR3 SO‑DIMM

- Max front side bus:		1333 MHz

- Memory installed:		4 GB, DDR3L‑1333 SO‑DIMM (1 x 4 GB)

- Storage type:			4 trays: 3.5‑inch SATA

- Hard drives installed:	4 x HDD max

- Network:			2 x 1 GbE RJ45 port

- Power supply:		220 VAC

- Power consumption:		(w/o hard drives) 37W max, 32W idle

- Form factor:			4‑bay mini tower

- USB ports:			4 x USB 3.0 port

- Network:			2 x Gigabit Ethernet LAN

- Operating temperature:	+10 °C to +35 °C

- Operating relative humidity:8 to 90% (non-condensing)

- Storage capacity:		Up to 16TB

- Fully featured video recording solution for up to 32 channels

### Network Video Recorder (Type 3)

- Processor:				Intel Pentium G6950 Dual Core (3M Cache, 2.8 GHz)

- Cache memory:			1 x 3 MB Level 2 cache

- Memory protection:			ECC Un-buffered

- Max front side bus:			1333 MHz

- Memory Installed:			4 GB, DDR3-1333 ECC UNB (2 x 2 GB)

- Storage Type:			8 Trays: 3.5-inch SATA

- Hard Drives Installed:		DIP-6082-8HD: 16 TB, 2 TB SATA/300 7.200 RPM 3.5“

            - DIP-6083-8HD: 24 TB, 3 TB SATA/300 7.200 RPM 3.5“

- SAS RAID Card:			2108 based SAS/SATA RAID card – 8 internal

            - ports / Low profile-PCI-E

- USB Ports:				4 USB 2.0: 2 in rear, 2 in front, (1 Type-A

            - Onboard)

- Network:				Dual Intel 82574L Gigabit LAN

- Form Factor:				2HU Rack Mount

- Power Supply:			740W Platinum Level Redundant

- System AC input VA requirement:	309.71 VA

- Total system power consumption:	284.94 W

- Operating Temperature:		+10 °C to +35 °C

- Operating Relative Humidity:	8 to 90% (non-condensing

- Storage capacity:			Up to 24 TB

- All-in-one recording solution for up to 128 channels (with 64 channels pre-licensed).

### Network Video Recorder (Type 4)

- Processor:				Intel Xeon Processor E3-1275 V3 (8 MB Cache, 3.5 GHz)

- Socket:				1

- Cache memory:			8 MB Intel Smart Caches

- Memory protection:			ECC Un-buffered

- Max front side bus:			1600 MHz

- Memory Installed:			8 GB, DDR3-1666 ECC UNB (1 x 8 GB)

- Storage Type:			8 Trays: 3.5-inch SATA

- Hard Drives Installed:		Data:	SATA-3, 7200 RPM, 64 MB, 3.5“, RAID-5

configuration

DIP-6183-4HD: 4 x 3 TB

DIP-6183-8HD: 8 x 3 TB

DIP-6184-4HD: 4 x 4 TB

DIP-6184-8HD: 8 x 4 TB

DIP-6186-8HD: 8 x 6 TB

DIP-6188-8HD: 8 x 8 TB

DIP-6180-00N: w/o HDD

OS:	2 x 120 GB SSD RAID-1 configuration

- SAS RAID Card:			8 ports LSI 3108 SAS3 controller

- USB Ports:				Front: 2 USB 2.0 ports

Rear: 2 USB 2.0 ports, 2 USB 3.0 ports

- Network:				Dual Intel i210AT Gigabit LAN

- Form Factor:				2HU rack mount

- Power Supply:			740W Platinum Level Redundant

- System AC input VA requirement:	272.7 VA

- Total system power consumption:	261.8 W

- Operating Temperature:		+10 °C to +35 °C

- Operating Relative Humidity:	8 to 90% (non-condensing

- Storage capacity:			Up to 64 TB

- All-in-one recording solution for up to 128 channels (with 64 channels pre-licensed).

### Network Video Recorder (Type 5)

- Processor:			Intel Xeon Processor E3-1275 V3 (8 MB Cache, 3.5 GHz)

- Cache memory:		8 MB Intel Smart Cache

- Memory protection:		ECC unbuffered

- Max front side bus:		1600 MHz

- Memory installed:		8 GB, DDR3-1666 ECC UNB (1 x 8 GB)

- Storage type:			16 Trays: 3.5-inch SATA

- Hard drives installed:	Data:	SATA-3, 7200 RPM, 64 MB, 3.5“, RAID-5

configuration

DIP-71F3-16HD: 16 x 3 TB

DIP-71F4-16HD: 16 x 4 TB

DIP-71F6-16HD: 16 x 6 TB

DIP-71F8-16HD: 16 x 8 TB

DIP-71F0-00N: w/o HDD

OS:	2 x 120 GB SSD RAID-1 configuration

- SAS RAID card:		8 ports LSI 3108 SAS3 controller

- USB Ports:			Front: 2 USB 2.0 ports

Rear: 2 USB 2.0 ports, 2 USB 3.0 ports

- Network:			Dual Intel i210AT Gigabit LAN

- Power Supply:		1200 W Platinum Level Redundant

- System AC input VA requirement:	402VA

- Power consumption:			385.9W

- Operating Temperature:		+10 °C to +35 °C

- Operating Relative Humidity:	8 to 90% (non-condensing

- Storage capacity:			Up to 128TB

- All-in-one recording solution for up to 128 channels (with 64 channels pre-licensed).

### Single / Quad Stream HD Decoder

- Video Standards:		MPEG-4

- Video Data Rate:		HD: 	Up to 20 Mbps (per stream)

SD: 	Up to 6 Mbps (single stream)

- Monitor resolutions:		DVI-I:	1920 x 1200 max (WUXGA)

HDMI:	1920 x 1200 max (WUXGA)

DP:	2560 x 1600 max (WQXGA)

- Network:			Protocols:	IPv4, UDP, TCP, HTTP, HTTPS, RTP/RTCP,

IGMP V2/V3, ICMP, ARP, DHCP, NTP (SNTP), digest authentication

Ethernet:	10/100/1000 Base‑T, auto-sensing, half/full duplex, RJ45

- Software Update:		Remote programmable

- Configuration:		Configuration Manager

- Interfaces

Video:			Video Outputs:	2 of 3 simultaneously

Connector:	 DVI-I, HDMI, DP, no VGA support

Standards:	H.264 (ISO/IEC 14496-10)

- Input Voltage:		220VAC

- Power Consumption:	135 W max

- Operating Temp:		0°C - 40°C Ambient temperature

- Humidity: 			0 - 90%, atmospheric humidity, noncondensing

- ONVIF conformant

### Indoor / Outdoor Day/Night HD 2 Mega Pixels IP vari-Focal Dome   cameras with PoE (Wide dynamic range)

- Input voltage:			 Power-over-Ethernet (48 VDC nominal) and/ or

+12 VDC ±10% (auxiliary)

- PoE IEEE standard:			802.3af (802.3at Type 1)

Power level: Class 3

- Power consumption:			7.2 W

- Current draw (PoE):			200 mA max.

- Current draw (12 VDC):		600 mA max.

- Sensor:				1/2.7‑inch CMOS

- Active Pixels:				1920 (H) x 1080 (V); 2MP (approx.)

- Dynamic range:			120 dB WDR

- Video Streaming:			Multiple configurable streams in H.264 and MJPEG,

configurable frame rate and bandwidth.

- Video compression:	 		H.264 (MP); M- JPEG

- Video Resolution (H x V):	 	1080p HD: 1920 x 1080

- White Balance:			2500 to 10000K, 4 automatic modes

- Shutter:				Automatic Electronic Shutter (AES)

- Day/Night:				Auto (adjustable switch points), Colour, Monochrome

- Backlight compensation:		On/off

- Signal-to-noise ratio (SNR):		>55 dB

- Noise reduction:			Intelligent Dynamic Noise Reduction with

separate temporal and spatial adjustments

- Intelligent defog:			Intelligent Defog automatically adjusts parameters for best

picture in foggy or misty scenes (switchable)

- Varifocal Lens:			2.8 to 13 mm Automatic Varifocal (AVF) SR lens

(IR corrected)

- Iris control:				Automatic iris control

- Operating temperature:		-30 ºC to +55 ºC for continuous operation

- Operating Humidity:		Up to 98% relative humidity

- Impact protection:			IK10

- Ingress protection:			IP 66

- ONVIF conformant:			Yes

### IP License Plate Camera

- Operational Range:			3.8 to 28.0 m

- IR Illumination:			Pulsed LED array, 850 nm

- Usable Plate Width:			100–170 pixels (with 4CIF encoding over capture range)

- Maximum Capture Speed:		225 km/h (140 mph). Must meet 30° mounting criteria.

- Sensor Type:				1/3-inch CCD, monochrome

- Active Pixels (PAL):			752 x 582

- Video Compression:			H.264 (ISO/IEC 14496-10); M-JPEG, JPEG

- Pixels CCIR: 				795 x 596 (HxV), EIA: 811 x 508 (HxV)

- Data Rate:				9.6 Kbps to 6 Mbps

- Resolution:				Horizontal x vertical:

4CIF: 704 x 576

- Frame Rate (per stream):		1 to 25 (PAL H.264)

1 to 25 (PAL M-JPEG)

- Dynamic Range:			120 dB (20-bit image processing)

- Lens:					5-50 mm varifocal, calibrated to optimal

capture distance

- PoE supply:				IEEE 802.3at compliant

- Input Voltage:			11-30 VDC, or 24 VAC ± 10%,

Power over Ethernet+ (IEEE 802.3at, class 4)

- Power Consumption:		PoE+: 13 W, maximum

11 W, typical

- Weatherproofing:			IP 67

- Operating temperature:		PoE+: -20 ºC to +50 ºC

- Cold Start-up Temperature:	–40°C, typically requires a 15- minute warm up prior to operation

- Operating Humidity:		0% to 100% relative, condensing

- Wind Load:				144 km/h

- ONVIF conformant:			Yes

### Day/Night HD 2 Mega Pixels IP vari-Focal box cameras with PoE (Wide dynamic range)

- Power Supply:			24 VAC 50Hz

12 VDC

Power Over Ethernet 48 VDC nominal

- Current Consumption:		400mA (12 VDC)

350mA (24 VAC)

150mA (PoE 48 VDC)

- Power consumption:			4.8W (12 VDC)

8.4W (24 VAC)

7.2W (PoE 48 VDC)

- PoE:					IEEE 802.3af (802.3at Type 1)

- Sensor:				1/2.7‑inch CMOS

- Active Pixels:				1920 x 1080

- Dynamic range:			76 dB Wide Dynamic Range

- Video compression:	 		H.264 (MP); M-JPEG

- Streaming:				Multiple configurable streams in H.264 and M-JPEG,

configurable frame rate and bandwidth.

- Resolution (H x V):	 		1080p HD: 1920 x 1080

- Day/Night:				Colour, Mono, Auto

- White Balance:			4 automatic modes, manual mode and measure

- Backlight compensation:		On/off

- Contrast enhancement:		On/off

- Intelligent defog:			Intelligent Defog automatically adjusts parameters for best

picture in foggy or misty scenes (switchable)

- Signal-to-noise ratio:			> 50 dB

- Dynamic Range:			Digital WDR: 76 dB

- Lens Mount:				CS mount (C-mount with adapter ring)

- Lens Types:				Manual and DC-Iris auto-detect with

Override DC-iris drive: max. 50 mA continuous

- Operating temperature:		-20 ºC to +55 ºC

- Operating Humidity:		20% to 93% relative humidity

- ONVIF conformant:			Yes

### CS Mount 2 Mega Pixels Lenses Day / Night Corrected (No Focus Shift)

- Maximum sensor format:		1/2‑inch

- Optical resolution:			5 Megapixels

- Focal length:				1.8 – 3mm, 3.8 – 13 mm and 5 – 55mm

- Iris range:				F1.4 to F8

- Min object distance:			0.3 m

- Lens mount:				C

- 4:3 Angle of view (HxV): 		97 x 72° Wide, 28 x 21° Tele

- Operation:				Focus: Manual

Zoom: Manual

Iris: 4-pin, DC control

- Application range:			Day/night

- IR corrected:				Yes

- Mount:				CS-Mount (Adjustable Lens Position)

- Flange Back:	 	 		12.5mm

- Operating Temperature:		-10°C ~ +50°C

- Operating Humidity:		Up to 93% non-condensing

### Thermal IP Camera

- Power supply:		24 VAC (SELV) ±10% 50Hz

- Current consumption:	1.4 A (24 VAC) max with all heaters on

3.1 A (24 VAC) max with all heaters on and PT at full load

- Image sensor:			Focal Plane Array (FPA), un-cooled Vanadium Oxide (VOx)

microbolometer Picture elements 320(H) x 240(V)

- Spectral response:		7.5 to 13.5 μm

- Thermal sensitivity:		< 60 mK at F1.0

- Scene range:			-40 °C to +160 °C

- Lens types:			9 mm, 13 mm, 19 mm

60 mm

- Video compression:		H.264 MP (Main Profile), H.264 BP+, MJPEG, JPEG

- Data rate:			9.6 kbps to 6 Mbps

- Resolution (H x V):		320 x 240

- Video Motion Analysis:	MOTION+, IVA

- Recording:			Continuous recording, ring recording.

Alarm/events/schedule recording

- Tamper protection:		Tamper switch integrated

- Operating temperature:	-50 °C to +55 °C

- Operating humidity:		20% to 93% RH

- Enclosure protection:	IP66

### Day/Night HD 2 Mega Pixels IP PTZ cameras with PoE (Wide dynamic range)

- Imager:				1/2.8-in.-type CMOS

- Imager:				Delivered: Approximately 2 megapixels

- Aspect Ratio:				HD: 16:9

- Lens:					20x optical zoom (4.7 to 94 mm)

- Focus:					Automatic

- Iris:					Automatic with manual override

- Digital Zoom				12x

- Wide Dynamic Range (WDR):	86 dB

- Signal to Noise Ratio:		> 50 dB (AGC off)

- Backlight Compensation:		On/Off

- Day/Night:				Monochrome, Colour, Auto

- Standards:				H.264 (ISO/IEC 14496‑10), M‑JPEG, JPEG

- Streaming:				Individually configurable streams in H.264 and

M‑JPEG, configurable frame rate and bandwidth;

- Data Rate:				9.6 kbps to 6 Mbps

- Resolutions (H x V):			1920 x 1080

- Signal-to-noise ratio:			> 50 dB

- Pan Range:				360° cont.

- Tilt Angle:				18° above horizon

- Input Voltage:			21 - 30 VAC 50Hz

- Power consumption:			55W

- Ingress Protection:			IP66

- Operating temperature:		-45 ºC to +55 ºC

- Operating Humidity:		0% to 100% relative, condensing

- ONVIF conformant:			Yes

### IR ILLUMINATOR

- LEDs:				High efficiency LED array with current limited integral power

circuit

- Number of LEDs:		18 high efficiency surface mount LEDs

- Wavelength:			850 nm or 940 nm

- Vertical angles:		10°

- Power consumption:		26 to 45 W (45 W max power)

- Input Voltage:		12 to 24 VDC or 24 VAC, 50/60 Hz

- Temperature Range:		-50 °C to +50 °C

- Environment:		IP67

- Power Cable:			To be supplied with IP67 power connector and 5 m

of connecting lead

- Color:				Black anodized heat sink with black front fascia

- Construction:			Robust, aluminum construction with acrylic front fascia

### Box Camera Housing

- Construction:					Aluminum casing, silicone gaskets, all stainless steel

hardware

- Colour:					Gray

- Window:					3 mm glass

- Locking clasps:				Tamper-resistant screws

- Camera mounting:				Removable camera/lens tray, mounted with two screws

- Operating temperature - External:		-30 °C to +50 °C

- Operating temperature - Internal:		-20 °C to +50 °C

- Enclosure protection:			IP67

- Power supply:					Power-over-Ethernet Plus (PoE+) IEEE

802.3at, 48 VDC nominal; or

12 VDC (switchable)

- Power consumption (housing only):	14 W max.

- Power handling (housing + camera):	30 W max.

- Supplied with a built-in heater and fan

### Box Camera Brackets

- Mounting Head:				Adjustable 360° pan, 180° tilt

- Colour:					Gray

- Maximum Load:				5 kg

### Small Video Wall Controller

- Processor:      			Single Intel Xeon W3505, 2.53 GHz, 4MB, 1066MHz

- Memory:      			2048MB, 1066MHz DDR3, Non ECC

- Hard Drive:      		500GB, 7200 Rpm, Serial ATA II (Excl recording)

- Optical Drive:		16X DVD+/-RW Drive

- Graphics Adapter:    	Dual Port 768 MB Quadro FX1800 Display Card

- Max Monitors/Controller:	4

- Max Images/Controller:  	25

- Max CPU Usage:    		50% with 25 simultaneous Images

### Large Video Wall Controller

- Processor:      			Dual Intel Xeon E5410 Quad Core, 2.33GHz, 12MB, 1333MHz

- Memory:      			4096MB, 667MHz DDR2 Quad Channel FBD

- Hard Drive:      		500GB, 7200 Rpm, Serial ATA II (Excl recording)

- Optical Drive:    		16X DVD+/-RW Drive

- Graphics Adapter:    	Dual Port SLI 768MB Quadro FX4600 Display Card

- Max Monitors/Server:	4

- Max Images/Server:  	50

- Max CPU Usage:    		50% with 50 simultaneous Images

### 2 X 2 Free Standing Video Wall Mount

- Screen array configuration: 		2 screens wide x 2 screens high.

- Centre of Display to Floor/Table Range: 	609.6mm (minimum bottom row)

22014mm (maximum top row)

- Colour: 					Black

- Manual Height Adjustment: 		Micro-adjustment up to 19 mm per screen

- Orientation: 					Landscape

- Plumb Adjustment: 				Micro-adjustment up to 19 mm

- Solution Type: 				Universal

- Typical Screen Sizes: 			42 - 50inch screens

### 3 X 3 Free Standing Video Wall Mount

- Screen array configuration: 		3 screens wide x 3 screens high.

- Centre of Display to Floor/Table Range: 	609.6 mm (minimum bottom row)

2696 mm (maximum top row)

- Colour: 					Black

- Manual Height Adjustment: 		Micro-adjustment up to 19 mm per screen

- Orientation: 					Landscape

- Plumb Adjustment: 				Micro-adjustment up to 19 mm

- Solution Type: 				Universal

- Typical Screen Sizes: 			42 - 46inch screens

## SYSTEMS CONTROL

### Control Room Workstation

- Processors: 		7th Generation Intel Core i5/i5k

7th Generation Intel Core i7/i7k

- Chipset: 		Intel Z270

Intel H270

- Memory:		Slot:	Four DIMM slots

Type:	DDR4

UDIMM

Speed:	2400 MHz

Configurations supported:	8 GB, 16 GB, 24 GB, 32 and 64 GB

- Ports and connectors

Back panel ports:

Network:	RJ45 port

USB:		Two USB 2.0 ports

Three USB 3.0 ports

One USB 3.1 Type-A port

One USB 3.1 Type-C port

Video/Audio:	One Surround Front Stereo port

One Surround Rear Stereo port

One Surround Center/Subwoofer port

One HDMI port for integrated graphics

One DisplayPort for integrated graphics

- Front panel ports:

Audio:		One Stereo Headphone jack•

One Microphone jack

USB:		Four USB 3.0 ports

Card Reader:	One 3-in-1 Card reader, supporting:

Secure Digital (SD)

Secure Digital Extended Capacity (SDXC)

Secure Digital High Capacity (SDHC) Classes 2,4 and 6

- Internal connectors:		PCIe Slots:	One PCIe x16 card slot

Two PCIe x1 card slots

One PCIe x4 card slot

M.2 Card:	One M.2 card slot for SSD

One M.2 card slot for Wi-Fi and Bluetooth combo card

- Communications:	Ethernet:	10/100/1000 Mbps Ethernet controller integrated on system board

Wireless:	Wi-Fi 802.11b/g/n

Wi-Fi 802.11ac

Bluetooth 4.0

- Audio:	Controller:	Integrated Realtek ALC3861 High Definition Audio with Waves MaxxAudio Pro

- Storage:			Interface:	SATA 6 Gbps for optical drive

SATA 6 Gbps for hard drive

M.2 for SSD

Hard drives:	Three 3.5-inch hard drives

Solid-state drive (SSD):	One M.2 slot

Optical drive (optional):	One Slimline DVD+/-RW

- Video Controller:		Integrated:	Intel HD Graphics 630

Discrete:	NVIDIA GT 730

NVIDIA GTX 745

NVIDIA GTX 1050 Ti

NVIDIA GTX 1070

NVIDIA GTX 1080

AMD Radeon RX 460

AMD Radeon RX 470

AMD Radeon RX 480

- Memory:			Integrated:	Shared system memory

Discrete:	Up to 8 GB GDDR5X

- Power ratings:		460W

Input voltage:	220 VAC

Input frequency:	50 Hz

Input current (maximum):	8A

- Relative humidity (maximum):	10% to 90% (non-condensing)

- Operating Temperature:		5°C to 50°C

### 24-inch High Performance HD LED Monitors

- Viewable image size (diagonal):		60.96 cm (24 inches)

- Pre-set display area:				Horizontal:		518.4 mm (20.3 inches)

Vertical:		324.0 mm (12.7 inches)

- Maximum resolution:			1920 x 1200

- Aspect Ratio:					16:9

- Pixel pitch:					0.270 mm

- Brightness (typical):				300 cd/m²

- Colour gamut (typical):			82%

- Colour depth:				16.7 million colours

- Contrast ratio (typical):			1,000:1

- Dynamic contrast ratio (estimate):		2 million:1

- Viewing angle (typical):			(vertical/horizontal):		178°/178°

- Response time (typical):			5ms (gray to gray)

- Panel type:					IPS (In-plane switching)

- Panel life:					30 000 hours

- Backlight:					LED

- Connectors:					VGA, USB, DVI-D (HDCP), DisplayPort

- AC input (voltage/frequency/current):	220 VAC/50 Hz /1.5A (maximum)

- Power consumption:				Normal operation, typical:	38W

- Operating Temperature:			0°C to +50°C

- Humidity:					0% to 90% Relative

### 42-inch High Performance HD LED Monitors

- Rated Voltage:				220VAC, 50Hz

- Power at Rated Voltage:			150 W

- Sync Format:					PAL

- LCD Panel:					LED

- Viewable Picture Area (Diagonal):		42 inch

- Active Display Area (H x V):		930.24 x 523.26 mm (36.6 x 20.6 in.)

- Pixel Pitch (H x V):				0.4845 x 0.4845 mm

- Resolution:					1920 x 1080

- Aspect Ratio:					16:9

- Display Colours:				1,073 million

- Response Time:				8 ms (typical)

- Backlight:					50,000 hours

- Luminance:					500 cd/m2 (typical)

- Contrast Ratio:				4000:1 (typical)

- Viewing Angle:				Horizontal/Vertical:	178°, typical

- Connectors:					VGA, HDMI, DVI-D

- Operating Temperature:			0°C to +50°C

- Humidity:					0% to 90% Relative

## NETWORK BACKBONE SYSTEM

### Server (Type 1)

| Form Factor: | 1U rack |
| --- | --- |
| Processors: | Intel Xeon processor E5-2400 product family |
| Cache: | 2.5MB per core; core options: 2, 4, 6, 8 |
| Memory: | Up to 192GB (6 DIMM slots): 2GB/4GB/8GB/16GB/32GB DDR3 up to 1600MT/s |
| I/O Slots: | 2 PCIe: One x8 PCIe slot with x4 bandwidth, 2.0, half-length, half-height One x16 PCIe slot with x16 bandwidth, 3.0, half-length, full-height |
| RAID Controller: | Internal Controllers: PERC S110 (SW RAID) PERC H310 PERC H710 External HBAs (RAID): PERC H810 External HBAs (non-RAID): 6Gbps SAS HBA |
| Drive Bays: | Up to eight 2.5” hot-plug SAS, SATA or SSD or four 3.5” SAS, SATA |
| Maximum Internal Storage: | Up to 16TB |
| Hard Drives: | Hot-plug Hard Drive Options: 2.5” SATA, nearline SAS, SAS (15K, 10K), SAS SSD, SATA SSD 3.5” SATA, nearline SAS, SAS (15K) Cabled Hard Drive Options: 3.5” SATA, nearline SAS, SAS (15K) Self-encrypting drives available |
| I/O adapter options | 1Gb Ethernet 10Gb Ethernet |
| Power Supply: | Hot-plug, redundant 350W and 550W power supplies |
| Availability: | High-efficiency, hot-plug, redundant power supplies; hot-plug hard drives |
| Systems Management: | IPMI 2.0 compliant OpenManage™ Essentials and Management Console OpenManage Power Center OpenManage Connections: OpenManage Integration Suite for Microsoft® System Center plug-in for VMware® vCenter™ HP Operations Manager, IBM Tivoli® Netcool®, and CA Network and Systems Management |
| Operating Systems | Microsoft® Windows Server 2012 Microsoft Windows Server 2012 Essentials Microsoft Windows Server 2008 R2 SP1, x64 (includes Hyper-V v2) Novell® SUSE® Linux Enterprise Server Red Hat® Enterprise Linux |

### Server (Type 2)

| Form Factor: | 1U rack |
| --- | --- |
| Processors: | Intel Xeon processor E3-1200 v6 product family |
| Chipset: | Intel C236 |
| Operating system: | Microsoft Windows Server® 2016, Microsoft® Windows Server 2012 Microsoft Windows Server 2012 R2, x64 Red Hat Enterprise Linux SUSE Linux Enterprise Server |
| Memory: | Architecture: Up to 2400MT/s DDR4 DIMMs Memory type: UDIMMs Memory module sockets: 4 Maximum RAM: Up to 64GB |
| Storage: | 2.5" SATA SSDs 2.5" SAS 15k HDDs 3.5" Enterprise SATA 7.2k HDDs 3.5" nearline SAS 7.2k HDDs |
| Drive Bays: | Up to 4 x 3.5" hot-swap HDD Up to 8 x 2.5" hot-swap HDD |
| Slots: | 2 x PCIe 3.0 slots + 1 slot for internal storage |
| RAID controllers: | Internal controllers: PERC S130, PERC H330, PERC H730, PERC H830 |
| Network controller: | 2 x 1GbE |
| Power Supply: | Up to 2 x 350W hot-plug redundant power supplies |
| Device access: | 5 total USBs: 2 Front; 2 rear; 1 internal |
| Systems management: | IPMI 2.0 compliant Dell OpenManage Essentials Dell OpenManage Mobile Dell OpenManage Power Center Dell OpenManage Connections: HP Operations Manager, IBM Tivoli Netcool and CA Network and Systems Management, Dell OpenManage Plug-in for Oracle Database Manager |

### L3 Gigabit Fibre switch with 24 Gigabit SFP slots and 2 combo ports (RJ45/SFP) (Core Switch)

- Physical Ports:		24 1000Base-X ports

2 Combo G (RJ-45/SFP) ports (2 10/100/1000Base-T)

1 RJ-45 console port

- Performance:			Switching Capacity: 48Gbps

Forwarding Rate: 35.7Mpps

MAC Address Table Size: 8K

Packet Buffer Size: 0.75MB

- L2 Features:			Auto-negotiation for port speed and duplex mode

Flow Control: IEEE 802.3x & Back-Pressure

Spanning Tree Protocol:

IEEE 802.1D Spanning Tree Protocol (STP)

IEEE 802.1w Rapid Spanning Tree Protocol (RSTP)

IEEE 802.1s Multiple Spanning Tree Protocol (MSTP)

Spanning Tree Fast Forwarding

Loopback detection

Auto edge port

BPDU filtering/guard

Root guard

VLANs:

Support 4K IEEE 802.11Q VLANs, port-based VLANs, protocol-based VLANs, IP-subnet based VLAN, GVRP Private VLAN

Link Aggregation:

- Static Trunk, IEEE 802.3ad Link Aggregation Control Protocol

- Trunk groups: 8

- Trunk links: 2~8 for Gigabit Ethernet port

- Trunk links: 2~4 for 10 Gigabit Ethernet port

IGMP Snooping:

- v1/v2/v3

- Immediate leave

- IGMP SNP leave proxy

- L2 Features:			2K IP Address entries

64 static routes and 512 net table

32 IP interface support

IP ARP RARP

Super-netting (CIDR)

RIPv1, RIPv2, and OSPF

IGMP v1/v2, PIM-DM , PIM-SM, DVMRP*

VRRP

- Management:			Switch Management:

- CLI via console port or Telnet

- WEB GUI management

- SNMP v1, v2c, v3

- IP clustering

Firmware & Configuration:

- Dual firmware images

- Firmware upgrade via TFTP/FTP/Xmodem

- Multiple configuration files

- Configuration file upload/download via TFTP/FTP server

- Supports RMON (groups 1, 2, 3 and 9)

- Supports BOOTP client

LLDP & LLDP-MED

- IPv6 Features:		IPv4/IPv6 Dual Protocol stack

IPv6 address type (unicast/multicast)

ICMPv6 and ICMPv6 redirect (host)

IPv6 neighbour discovery

Stateless and statefull auto configuration

SNMP, HTTP, SSH, Telnet over IPv6

IPv6 syslog and TFTP support

- Temperature:			0℃ to 45℃ (Standard Operating)

- Humidity:			5% to 95% (Non-condensing)

### Managed 24 Port 10/100/1000 Head End Switch

- Switch layer:						L3

- Basic switching RJ-45 Ethernet ports qty: 	24

- Basic switching RJ-45 Ethernet ports type:	Gigabit Ethernet (10/100/1000)

- SFP+ module slots quantity: 			2

- Console port: 					RJ-45

- Copper Ethernet cabling technology: 		1000BASE-T, 100BASE-TX, 10BASE-T

- USB 2.0 ports quantity: 				1

- Networking standards: 			IEEE 802.1ab, IEEE 802.1D, IEEE 802.1p, IEEE

802.1Q, IEEE 802.1s, IEEE 802.1v, IEEE 802.1w, IEEE 802.1x, IEEE 802.2, IEEE 802.3, IEEE 802.3ab, IEEE 802.3ac, IEEE 802.3ad, IEEE 802.3ae, IEEE 802.3az, IEEE 802.3u, IEEE 802.3x, IEEE 802.3z

- Full duplex: 				Yes

- 10G support:				Yes

- VLAN support:			Yes

- Port mirroring:			Yes

- Link aggregation:			Yes

- Switching capacity:			212 Gbit/s

- Throughput:				158 Mbps

- Management protocols:		SNMP v1/v2/v3

- Form factor:				1U

- Internal memory:			1024 MB

- Operating temperature: 		0° to 45° C

- Operating relative humidity:	5% - 85%

- Power supply: 			220VAC, 50Hz voltage

- Power consumption (typical) 	52.8 W

### Managed 24 Port 10/100/1000 Field Switch with PoE

- Port types: 				24 x 10/100/1000 + 2 x 10 Gigabit SFP+ + 2 x combo Gigabit

SFP

- Power Over Ethernet (PoE):	PoE+

- Capacity: 				MAC addresses : 16384

IPv4 routes (static) : 1024

IPv6 routes (static) : 1024

IPv4 routes (dynamic) : 8160

IPv6 routes (dynamic) : 4096

Maximum member ports per LAG : 8

Maximum dynamic ports per switch stack : 144

LAG groups : 128

OSPF routes : 8160

RIP routes : 512

ECMP next hops per route : 4

ECMP groups : 64

VLAN routing interfaces : 128

VLANs supported : 4094

Multicast entries (IPv4) : 512

Multicast entries (IPv6) : 256

ARP entries : 6144

NDP entries : 400

ACL : 100

Maximum rules per ACL : 1023

Max ACL rules system-wide : 4096

Maximum ACL rules per interface (IPv4) egress rules : 1024

Maximum ACL rules per interface (IPv4) ingress rules : 3072

Maximum ACL rules per interface (IPv6) egress rules : 512

Maximum ACL rules per interface (IPv6) ingress rules : 1021

Maximum VLAN interfaces with ACLs applied : 24

- RAM:					1 GB

- Flash Memory: 			256 MB

- MAC Address Table Size:		16K entries

- Routing Protocol:			OSPF, RIP-1, RIP-2, IGMPv2, IGMP, VRRP, PIM-SM, PIM-

DM, IGMPv3, OSPFv3, MLDv2, MLD

- Advanced Switching:		Layer 3

- Features:				Broadcast Storm Control, Dynamic VLAN Support (GVRP),

Protocol-based VLANs support, Quality of Service (QoS), Rapid Spanning Tree Protocol (RSTP) support, Weighted Round Robin (WRR) queuing, auto-negotiation, dual firmware images, flow control, layer 2 switching, layer 3 switching, port forwarding, Energy Efficient Ethernet, port mirroring, redundant fans, stackable, tagged VLAN, Generic VLAN Registration Protocol (GVRP), LLDP support, Link Aggregation Control Protocol (LACP), MDI/MDI-X switch, Multiple Spanning Tree Protocol (MSTP) support, Network Access Control (NAC), Per-VLAN Rapid Spanning Tree (PVRST)

- Compliant Standards:		IEEE 802.1D, IEEE 802.1Q, IEEE 802.3, IEEE 802.3ab, IEEE

802.3ac, IEEE 802.3ad (LACP), IEEE 802.3ae, IEEE 802.3az, IEEE 802.3u, IEEE 802.3x, IEEE 802.3z, IEEE 802.1ab (LLDP), IEEE 802.1ag, IEEE 802.1p, IEEE 802.1s, IEEE 802.1v, IEEE 802.1w, IEEE 802.1x, IEEE 802.2

- Remote Management:		Protocol HTTP, RMON, SNMP, SNMP 2, SSH

- PORTS (2ND): 			2 x 10 Gigabit SFP+

- PORTS (3RD): 			2 x combo Gigabit SFP

### 8 Port 10/100/1000TX High-Power PoE and 2 Gigabit Combo SFP (Field Switch)

- Standards:			IEEE 802.3

IEEE 802.3u

IEEE 802.3z

IEEE 802.3x

IEEE 802.3ad

IEEE 802.1D

IEEE 802.1w

IEEE 802.1s

IEEE 802.1Q

IEEE 802.1p

IEEE 802.1ad

IEEE 802.1AB

IEEE 802.3af

IEEE 802.3at

- Connectors:		 	(8 )10/100/1000 RJ-45

(2) 100/1000 SFP ports

- Protocols:			 CSMA/CD

- Technology:			Store-and-forward switching architecture

- MAC Address:		8K MAC address table

- Backplane:			20 Gbps

- Power Input:			Internal power: 220VAC

- Power-over-Ethernet:	Max PoE power budget 75 Watts

Max output power per port up to 30 Watts

Data-pairs mode

Max current: 1.7A

Provide power on all 8 copper ports

- Environment Operating: 	0°C to 50°C

- Humidity: 			10% to 90% (non-condensing)

### Industrial 10-Port Managed PoE Ethernet Switch with 8* 10/100TX 802.3af PoE + 2*Gigabit combo SFP port (Field Switch)

- Standards:		 	IEEE 802.3 10Base-T Ethernet; IEEE 802.3u 100Base-

TX/FX; IEEE802.3ab 1000Base-T; IEEE802.3z Gigabit fibre; IEEE802.3x Flow Control and Back Pressure;

IEEE802.3ad Port trunk with LACP; IEEE802.3af Power over Ethernet; IEEE802.1d Spanning Tree/IEEE802.1w Rapid Spanning Tree; IEEE802.1p Class of Service;

IEEE802.1Q VLAN Tag; IEEE 802.1x User Authentication (Radius); IEEE802.1ab LLDP

- Switch Architecture:		Back-plane (Switching Fabric): 5.6 Gbps

Packet throughput ability

(Full-Duplex): 8.3M pps@64 bytes

- Transfer Rate:		14,880 pps for Ethernet port

148,800 pps for Fast Ethernet port

1,488,000 pps for Gigabit Ethernet port

- Packet Buffer:	 	1 Mbits

- MAC address:		 8K MAC address table

- Flash ROM:			4 Mb

- DRAM:			32 Mb

- Connector:			10/100TX: 8 x RJ-45

10/100/1000T: 2 x RJ-45

SFP Combo ports: 2 x 100/1000 SFP

RS-232 connector: RJ-45 type

- PoE Pin Assignment:	RJ-45 port # 1~# 8 support IEEE 802.3af End-point,

Alternative A mode. Per port provides 15.4W ability.

- Protocol:			CSMA/CD

- Power Supply:		External Power Supply: DC 48V, Redundant power DC

48V, removable terminal block

- Power Consumption:	 136 Watts (Full Load)

- Operating Humidity:	 5% to 95% (Non-condensing)

- Wide Operating Temperature:	-40°C ~ 65°C

### Single-mode Fibre` SFP Gigabit Adapter Kits

- Connector type:			LC

- Wavelength:				1310 nm

- Transceiver form factor:		SFP

- Temperature Operating: 		-40°C ~ 70°C

- Humidity Operating: 		10% to 90% Non-condensing

- Power consumption typical:		0.9 W

- Power consumption maximum:	1 W

- Cable type:				Single-mode

- Cable length:				2m to 10km

### Multi-mode Fibre` SFP Transceiver

- Capacity:				100Mbps half-duplex (200Mbps full-duplex)

- Fiber Type:				62.5/125um Multi-mode

- Maximum Cable Distance:		2km

- Wave Length:			1310nm

- IEEE:					802.3u 100BASE-FX

- Temperature Operating: 		-40°C ~ 70°C

- Humidity Operating: 		10% to 90% Non-condensing

- Power Budget:			13dB

- Power Voltage:			3.3V

- Output Optical Power:		Max:	-14dBm

Min:	-19dBm

### KVM Extenders (Dual View – Cat Cable Link)

- Receivers

- Max. Video Resolution:		WUXGA (1920 x 1200)

UXGA (1600 x 1200)

- Extension Distance:			200m

- Unit Connection:			CAT-RJ45 Female x 1 (VGA+KB/MS)

CAT-RJ45 Female x 1(VGA

Keyboard USB-A x 1

Mouse USB-A x 1

Monitor HDB15-Female x 2 (Blue)

Audio Jack (Speaker + Mic) 1 Set

Serial DTE x 1

- Mask Hotkey Switch:		x 1

- Power Consumption (Max.):	DC 9-12V, 600mA

- Temperature Operating: 		5°C ~ 45°C

- Humidity Operating: 		< 80 %, non-condensing

- Transmitters

- Max. Video Resolution:		WUXGA (1920 x 1200)

UXGA (1600 x 1200)

- Extension Distance:		200m

- Unit Connection:		CAT-RJ45 Female x 1 (VGA+KB/MS)

CAT-RJ45 Female x 1(VGA

HDB15 Female x 1 (Grey: VGA+KB/MS)

HDB15 Female x 1 (Blue: VGA only) Audio Jack (Speaker + Mic) 1 Set

Serial DCE x 1

- Mask Hotkey Switch:		x 1

- Power Consumption (Max.):	DC 9-12V, 600mA

- Temperature Operating: 	5°C ~ 45°C

- Humidity Operating: 		< 80 %, non-condensing

### KVM Extenders (Dual View – Fibre Optic Cable Link)

- Receivers

- Max. Video Resolution:		WUXGA (1920 x 1200)

UXGA (1600 x 1200)

- Extension Distance:		1 Km

- Unit Link:			Link Connectors:	4 SC connectors

Fiber Type: 		Multi-Mode

- Unit Connection:		USB-A x 2

DVI-Female x 2

Audio Jack (Speaker + Mic) 1 Set

Serial DTE x 1

- Power Supply:			External Power Adapter DC 12V

- Temperature Operating: 	5°C ~ 45°C

- Humidity Operating: 		< 80 %, non-condensing

- Transmitters

- Max. Video Resolution:		WUXGA (1920 x 1200)

UXGA (1600 x 1200)

- Extension Distance:		1 Km

- Unit Link:			Link Connectors:	4 SC connectors

Fiber Type: 		Multi-Mode

- Unit Connection:		USB-B: 		USB mouse

DVI-Female x 2

Audio Jack (Speaker + Mic) 1 Set

Serial DTE x 1

- Power Supply:			External Power Adapter DC 12V

- Temperature Operating: 	5°C ~ 45°C

- Humidity Operating: 		< 80 %, non-condensing

### KVM Extenders (Quad View – Cat Cable Link)

- Receivers

- Resolution:			Up to 1920 x 1200 @ 50Hz, 1080p

- Extension Distance:		140m

- Unit Connection:		4 × DVI-I socket

4 x USB-A

4 × RJ 45 socket

Audio:	2 x 3.5mm

Serial:	1 x DB9(M)

- Power:				220VAC, 50Hz, 5.0VDC / 4A

- Temperature Operating: 	5°C ~ 45°C

- Humidity Operating: 		80% non-condensing max.

- Transmitters

- Resolution:			Up to 1920 x 1200 @ 50Hz, 1080p

- Extension Distance:		140m

- Unit Connection:		4 × DVI-I socket

2 x USB-B

4 × RJ 45 socket

Audio:	2 x 3.5mm

Serial:	1 x DB9(F)

- Power:				220VAC, 50Hz, 5.0VDC / 4A

- Temperature Operating: 	5°C ~ 45°C

- Humidity Operating: 		80% non-condensing max.

### KVM Extenders (Quad View – Fibre Optic Cable Link)

- Receivers

- Resolution:			Up to 1920 x 1200 @ 50Hz, 1080p

- Extension Distance:		10Km on SM Fiber

(200m) w/ 62,5μm Multimode-Fiber

(400m) w/ 50.0μm Multimode-Fiber

- Unit Connection:		4 × DVI-I socket

4 x USB-A

4 Duplex-LC

Audio:	2 x 3.5mm

Serial:	1 x DB9(M)

- Power:				220VAC, 50Hz, 5.0VDC / 4A

- Temperature Operating: 	5°C ~ 45°C

- Humidity Operating: 		80% non-condensing max.

- Transmitters

- Resolution:				Up to 1920 x 1200 @ 50Hz, 1080p

- Extension Distance:			10Km on SM Fiber

(200m) w/ 62,5μm Multimode-Fiber

(400m) w/ 50.0μm Multimode-Fiber

- Unit Connection:			4 × DVI-I socket

2 x USB-B

4 Duplex-LC

Audio:	2 x 3.5mm

Serial:	1 x DB9(F)

- Power:				220VAC, 50Hz, 5.0VDC / 4A

- Temperature Operating: 		5°C ~ 45°C

- Humidity Operating: 		80% non-condensing max.

### Fibre Optic Splice Dome Closure

- Cables Entry & Exit:				3 & 3

- Max Capacity of Cores Per Splice Tray:		12 (Single) / 16 (Single) /72 (Ribbon) 96 single

(24 core trays x 4)

- Max Capacity of Splice Trays/ Closure 		4

- Max Capacity of Core Single: 			48 (12Cores/Tray x4)/ 72 (24 Cores/Tray x3),

96(24 core tray x 4)

- Sealing Structure of Cable Entry Port:		Heat-shrinkable

- Sealing Structure:					Sealing Structure Silicon Gum Material

- Temperature Operating: 				-20°C ~ 80°C

### Fibre Optic Patch Panel / Splice Box

- Capacity: 					Maximum 12/24/48 cores

- Adapters output: 				12/24/48 core

- Environment temperature: 			-10°C ~+60°C

- Humidity:					0-90%, non-condensing

- Multimode Insertion Loss:			0.2dB Maximum

- Single-mode Insertion Loss:			0.2dB Maximum

- Multimode Adaptor Wavelength:		850 to 1300nm

- Single-mode Adaptor Wavelength:		1310 to 1550nm

- Connector Type:				ST/SC/LC

- Panel Type:					Sliding

- Single/Multimode:				Single/Multimode

- Simplex/Duplex:				Simplex/Duplex

- Rack Height:					1U

### Floor Standing 19” Racks

- Nominal height:			21U, 24U, 27U, 33U, 38U, 42U or 47U (1U = 44.45mm).

- Outer width:				800mm

- Outer depth:				1000mm

- Maximum load capacity:		1000kg

- Protection class:			IP40

- Front doors:				Perforated steel curved front doors

- Back doors:				Two-leaf perforated steel back doors

- Side panels:				Full steel dismounted on latches with a lock assembly option

- Cable ducts:				Five brush ducts in the ceiling

Eight cable ducts in the floor

- Cable organizer:			2 pcs - mounted on rack rails

- Frame thickness:			1.5mm

- Mounting rail thickness:		2.0mm

- Door thickness (steel):		1.2mm

- Side panel thickness:			1.2mm

- Base thickness:			1.2mm

- Top cover thickness:			1.2mm

- Shelf: 					2 pcs

- Vertical organizer: 			2 pcs

- Power strip: 				1 pc

- Fans: 					4 pcs

- Lock: 					2 pcs

- Wheels: 				4 pcs

- Feet: 					4 pcs

- Protection against rust, oxidation, scratches, corrosion

### Wall Mount 19” Swing Rack

- Nominal height:			4U, 6U, 9U, 12U, 15U, 18 (1U = 44.45mm).

- Outer width:				600mm

- Outer depth:				600mm

- Mounting depth:			275mm

- Maximum load capacity:		60kg

- Protection class:			IP20

- Front doors:				Glass with a lock

- Side panels:				Full steel dismounted on latches with a lock assembly option

- Cable ducts:				2 pcs - ceiling and floor

- Frame thickness:			1.2mm

- Mounting rail thickness:		1.5mm

- Door thickness (steel):		1.2mm

- Glass thickness:			5.0mm

- Side panel thickness:			1.2mm

- Base thickness:			1.2mm

- Cover thickness:			1.2mm

- Fans: 					2 pcs

- Earth points: 				2

- Protection against rust, oxidation, scratches, corrosion

### 19” Rack Accessories

- Cooling fan Unit

- Performance:				195m3/h

- Noise level:				<48dB

- Height:				38mm

- Width:				120mm

- Depth:					120mm

- Colour:				Black

- Housing:				Aluminium housing

- Brush Panels

### Construction

- Panel: 0.060 Aluminum

- Finish: Black Powder Paint

- Brush: Nylon

- 50mm Base plate

- Cat6/6e Brush Panels

- 24-Port Patch Panel:			16 GA CRS

- Jack Housing:			High Impact, Flame Retardant Plastic, UL 94V-0

- Spring Wire:				Phosphor Bronze

- 110 Connector:			Phosphor Bronze Alloy with 100 micro-inch Alloy

- Gold Rating:				50 Micro-inches of Gold over 100 micro inches of

Nickel

- Surface Finish:			Black Powder Coat

- Mating Force:			100 Grams MIN/Contact

- Temperature Range:			-40° ~ 70°C

- Plug Retention in Jack:		50N (11 LBS SQ)

- Current Rating:			1.5 AMP DC

- Contact Resistance:			2.5 MILOHMS MAX

- Cable Routing Panels.

- Product Type:		Rack cable management panel (horizontal)

- Product Material:		Steel

- Colour:			Durable black powder coated finish

- Rack Size:			19inch

- Cable Routing Rings.

| No. of Rack Spaces | 1 |
| --- | --- |
| Material | Steel |
| Colour | Black |
| Width (mm) | 483 |
| Height (mm) | 43.7 |
| Depth (mm) | 86 |

- Cable Jumper Ring Bracket.

| Accessory Type | D-ring |
| --- | --- |
| Height (mm) | 43.18 |
| No. of Rack Spaces | 1 |
| Material | Polycarbonate |
| Colour | Black |
| Width (mm) | 222 |
| Depth (mm) | 143.7 |

- Shelves.

| Frame Type: | Steel |
| --- | --- |
| Mounting Options: | Front Mount (Front and Rear) |
| U Height: | 1U |
| Weight Capacity (Stationary): | 79.6 kg |
| Colour: | Black |
| Enclosure Type: | Steel |
| External Depth: | 700 mm |
| External Height: | 43.7 mm |
| External Width: | 482 mm |
| Maximum Mounting Depth: | 974 mm |
| Minimum Mounting Depth: | 495 mm |
| Rail Thickness: | 1.2 mm |

- Blank Panels.

| U Height: | 1U / 2U / 3U / 4U |
| --- | --- |
| Colour: | Black |
| Enclosure Type: | Steel – Vented or Solid |
| External Depth: | 15 mm |
| External Height: | 88.1 mm |
| External Width: | 482 mm |

- Power Strips (Multi Plugs)

- Nominal Output Voltage:			230V

- Maximum Total Current Draw:		16A

- Output Connections:				(12) IEC 320 C13 (Battery Backup)

- Nominal Input Voltage:			230V

- Input frequency:				50Hz

- Input Connections:				IEC-320 C20

- Cord Length:					2.5meters

- Number of Power Cords:			1

- Load Capacity:				3680VA

- Maximum Input Current:			16A

- Rack Height:					1U

- Operating Temperature:			0° ~ 45°C

- Operating Relative Humidity:		0 - 95 %

### Field Node Box (Kiosk) - Weatherproof Metal Cabinets

- Door Lock Type:				Double Bar

- Gland Plate:					Yes

- Fixing Kit:					Yes

- External Dimensions:			1000 x 800 x 300mm

- Ingress Protection:				IP 66

- Impact Resistance:				IK 10

- UV Resistance:				UL 508

- Flammability Rating (UL 746 C 5):	UL 94 5V

- Electrical Insulation:			Totally Insulated

- Temperature:					-40°C to 70°C

- Fire retardant:				Polypropylene RAL 7035

- Loading Capacity:				1200kgs

- Materials:					High-quality cold rolled steel

- Thickness:					Cabinet:	1.6mm mild steel

Mounting rails:	2mm 304 mild steel

Doors:			1.6mm mild steel

- Cooling Fans:					Four standard 120mm AC cooling fans

- Doors:						Front and rear with built-in washable air filter

- Surface finish:				Degreasing, pickling, phosphating powder coating

- 6 mm² earth connection

## INTERCOM SYSTEM

### Audio Server

- Power:				220VAC, 4W max.

- Temperature range:		 	-15°C - +55°C

- Relative humidity:			95%

- Processor subsystem:		Intel IXP425 with HW acceleration for packet processing and

encryption

- Media subsystem:			DSP @ 1600 MIPS

FPGA @ 400K gates

- Storage subsystem:			Solid state (64 MB Flash)

SIM card (IP configuration, HW-ID)

- Memory:				128 MB SDRAM

1 MB NVRAM

- Subscriber Capacity:		552 intercom stations per server

- Busy Hour Call:			60 000 BHCA

- IP Telephones:			552 IP telephones per server

- IP security:				SSH, HTTPS, firewall

- SIP:					RFC 3261, SIP INFO, RE-Invite

RFC 2833, RFC 4733,

- VoIP Internal Networking:		30 channels

- VoIP External Networking:		30 channels

- Configuration:			AlphaPro over IP, Web

- Monitoring and logging:		SNMP trap, SNMP MIB, syslog, Web, e-mail, SqLite

- Open Duplex Conference:		20 open duplex conferences can be configured

A maximum of 16 subscribers can participate in conference simultaneously.

- Push to Talk Conference:		50 conference channels Unlimited number of participants

Priority features

- Group Call 250 groups:		Unlimited number of participants Priority features

- Call Modes:				Open mode

Ringing mode

Call request mode

Priority features

- Audio messaging:			PA broadcasting

Auto-attendant,

Voice guidance (doors, elevators)

Security voice response

### IP Desktop Master Station with Display & Handset

- Ethernet:			1 x RJ45 10/100 Mbps with PoE

- IP protocol:			 IP v4 – TCP – UDP – HTTPS – TFTP – RTP – RTCP – DHCP –SNMP – DiffServ – TOS – STENTOFON CCoIP - SIP

- LAN protocol:		Power over Ethernet (IEEE 802.3 a-f)

VLAN (IEEE 802.1pq) / network access control (IEEE 802.1x)

STP (IEEE 802.1d) / RSTP (IEEE 802.1d-2004)

- Audio:				Wideband 200Hz – 7kHz (G.722) / telephony 3.4kHz (G.711)

Acoustic echo canperimetering / open duplex / adaptive jitter filter /

Active noise filtering

1.5W speaker output @ 8 Ohm

- Video:				Only supported in AlphaCom environments

Codecs supported: MJPEG Resolution: 320 x 240 (qVGA)

- Management:			HTTPS (web interface)

DHCP and static IP

Automatic remote update

Centralized monitoring

Status LEDs

- Display:			3.5“ Transmissive TFT with touchscreen panel

Active area 70 x 52.5mm

320 x 240 dots

262.000 colors

LED backlight (white)

- Operational voltage:		Power over Ethernet: IEEE 802.3 a-f, class 0

- Power input:			Circa 10 W

- Environmental conditions”	-20°C to +55°C

### SIP Phone

- SIP: 						Compliance per IETF RCF 3261

DTMF signaling: SIP INFO

Calling name presentation

Calling number presentation

- Audio:						Narrowband audio (3.4 KHz) – G.711 A and ì law

Wideband audio (3.4 KHz) – G.722

Adaptive jitter buffer

- Network QoS:		 		Diffserv, TOS

- Ethernet Network Interface: 		10/100 Mbps, Base-T, RJ45

- IP transport: 					RTP/RTCP per IETF RFC 3550 and 3551

- IP telephone interoperability: 		Grandstream

SNOM

Cisco

ATCOM

- IP DECT interoperability: 			SNOM

Ascom

Polycom KIRK

Cobs

- IP Software phone interoperability: 	X-Lite Version 3.0

### Sub-station IP with 1 Button

- Protection: 				Vandal resistant design 2 mm stainless steel front plate

Tamper proof fastening screws, buttons and loudspeaker grills

- Call button: 				16 mmØ stainless steel

- Power: 				Power over Ethernet, IEEE 802.3 a-f

Local power (19-27 VDC)

Max. 8W

- Connectors: 				2xRJ45 (Ethernet) 10/100 Mbit/sec.

Pluggable screw terminals.

- IP protocols: 				IP v4 - TCP - UDP - HTTP - RTP - RTCP -

DHCP - DiffServ - TOS – STENTOFON CCoIP

- Audio technology: 			Wideband 200 Hz - 7 kHz (G.722)

Telephony 3.4kHz (G.711)

Acoustic echo canperimeteration

Open duplex

Adaptive jitter filter

1.5Watt audio output

External audio output (0 dB, 600 ohm)

- Installation: 				Remote automatic software upgrade

Centralized provisioning

DHCP and static IP

Integrated web server

- Operation: 				Network supervision

VoIP statistics

Centralized monitoring, Tone test

- Advanced features: 			Dual port Ethernet switch for connecting CCTV cameras and

other IP stations.

Programmable inputs, (closing contact) or monitoring door status and alarms if not used for call buttons.

Programmable relay output for door control, switch on beacon, etc. (1A at 24V DC)

### Rainshield Stainless steel

- Construction:			Stainless Steel

- Installation:			Gooseneck / Surface Mount

### Stainless Steel Intercom Gooseneck with Baseplate

- Construction:			Stainless Steel gooseneck for superior durability

Universal mounting plate

- Dimensions:    		51mm diameter x 1355mm total height x 280mm overhang

## PERIMETER INTRUSION DETECTION SYSTEM

### Kinematics Detection System

### D221 - 2 Wire Insens Sensor.

- Power: 				24V, 4mA supplied via 2-Wire interface

- Surge Protection:			Gas Arrestor, Inductor, Tranzorb. Class 3.

- Communication Protocol: 		2W proprietary @ 38Kbps

- Data Conversion:			Data onto Power

- Operating Temperature: 		-20°C to 70°C

### L2W.

- Surge Protection: 			Gas Arrestor, Inductor, Tranzorb, Class 3.

- Communication Interface 1: 		Moduteq 2W proprietary @ 38Kbps

- Communication Interface 2: 		RS485 @ 1.84 Mbps Max. amount of Devices: - 200

- Power (input): 				Input 24V, 24W Max(depending on connected devices)

supplied by Linkbus

- Power (output): 				Input 24V, 24W Max on 2W interface

- Max cable length:			500 meter (OEM Approved Maximum).

- Max 2W Devices: 			32.

- Over Current protection: 		Yes

- Operating Temperature: 		-20°C to +70°C

- Ingress Protection:			IP65 rated enclosure if mounted outdoors

### LC - Linkbus ↔ Ethernet Bridge.

- Data Conversion:				Linkbus ↔ TCP/IP over 10/100 Ethernet.

- Module Power Requirements:		100mA Max, 24VDC

- Communication Protocol: 			RS485

- Communication Speed: 			1.84 Mbps

- Operating Temperature: 			-20°C to +70°C

- IP Rating: 					30

### LCX - Controller.

- Power Requirements: 			24V

- Communication Protocol: 			RS485

- Communication Speed: 			1.84 Mbps

- Operating Temperature: 			-20°C to +70°C

- IP Rating: 					30

### LOM - Linkbus ↔ Multimode Fibre Bridge.

- Data Conversion: 				Linkbus ↔ Multimode Fiber Communication

- Power Requirements: 			24V

- Communication Protocol: 			RS485

- Communication Speed: 			1.84 Mbps

- Max. amount of Devices:			200

- Operating Temperature: 			-20°C to +70°C

- IP Rating: 					30

### PSU220/24 - Linkbus Power Supply Unit.

- Input Voltage: 			85-264 VAC

- Input Frequency: 			47-63 Hz

- Input Current: 			0.85 A Max. @ 230 VAC

- No Load Input Power: 		0.48 W Max.

- Output Voltage:			24 VDC

- Max. Output Current: 		2.5 A (Nominal), 3.1 A (Peak)

- Line Regulation: 			±0.5% Max.

- Load Regulation: 			±1% Max.

- Over Voltage Protection: 		Trip @ 29 VDC

- Short Circuit Protection: 		Trip & Restart.

- Operating Temperature: 		-10°C to +70°C

- Cooling: 				Natural convection

### LPI - Linkbus PSU Interface

- Input Voltage (From PSU220/24: 			24 VDC

- Max. Input Current: 				2.5 A (Nominal), 3.1 A (Peak)

- Surge Protection: 					Class 3 - Inductor, Gas Arrestor, Tranzorb

- Output Voltage: 					24 VDC

- Max. Output Current: 				2.5 A (Nominal), 3.1 A

- Operating Temperature: 				-10°C to +70°C

### Advanced Acoustic Detection System

### Environmental operating range

The system shall operate within specifications under the following environmental conditions:

- Temperatures between -40°C to +70°C

- Relative humidity between 0 and 95%, non-condensing

### Powering options

The processor shall operate at 12 VDC, and shall accept input power from two types of supplies, a DC power/float charger or a centrally located low voltage DC power source.

- DC power/float charger

A DC power/float charger shall be provided to supply 13.5 VDC to the processor and to charge a back-up battery. The float charger shall be available in 230VAC, 50 Hz. The float charger shall be capable of being plugged into a standard AC power source.

- Back-up battery

The processor shall include a rechargeable 12 VDC, 0.8 amp hour, gel-cell,

back-up battery. The back-up battery shall be capable of being charged by the DC power/float charger.

- Centrally located low voltage DC power source

For multiple processors deployed around a large perimeter, or a single processor that requires a long power feed cable, a centrally located DC power source shall be a viable power supply option. The processor shall be capable of receiving DC power from 18 VDC, 50 mA (minimum) to 56 VDC, 15 mA (maximum) sources. A 24 VDC power supply (85 to 245 VAC, 50/60 Hz @ 1.25 A) shall be available as an option.

## SURGE PROTECTION DEVICES (SPDs)

### Class 1 high energy Metal Oxide Varistor (MOV) - (Power Protection: Lightning Protection:)

For protection against partial direct and indirect lightning strikes.

- Certified under; tested to:			UL 1449, (UL file E213469); IEC - 61643-1

- Class (IEC):					I, II

- Max permitted operating voltage:		275/350V

- Nominal discharge current (8/20) In:	70kA

- Max discharge current (8/20) lmax:		150kA

- Max discharge current (10/350) limp:	25kA

- Protection level Up-at limp (10/350):		1.2kV

- Response time tA:				<25 ns

- Back-up fuse (if mains is > 250A):		250Agl

- Short - circuit capability to:			25kA / 50Hz

- Temperature range:				-40°C to +80°C

- Location of use: 				Main distribution boards (First incoming point).

### Class 2 Silicon Avalanche Diode (SAD) - (Power Protection: Critical Electronic)

For protection of sensitive digital equipment.

- Certified under; tested to:			IEC 61643-1

- Class (IEC):					Class II

- Max permitted operating voltage:		250 VRMS

- Nominal discharge current (8/20) In:	15kA

- Max discharge current (8/20) lmax:	20kA

- Protection Level UP:				480V

- Response time tA:				<5 ns

- Temperature range:				-40°C to +80°C

- Degree of Protection:			IP 20

- Location of use: 				Sub-distribution boards or as close as possible to a

protected device (Internal Distribution Point)

## CABLING

### Category 6 or Cat 6 cable

- Speed:				10/100/1000MbE, 10GbE (Shorter Distances or Cat6a Required for 10GbE)

- Frequency:			Up to 550 MHz

- Performance:			SNR higher

- Maximum Cable Length:	100 meters; 10GbE over shorter distances.

### FIRE RESISTANT CABLE – PH30 (STANDARD)

- Conductor: 			1.5mm² High conductivity annealed stranded plain bunched copper

wire or solid plain copper wire.

- Insulation: 			High temperature fire resistant core wrapping with halogen free

compound

- Insulation Colour: 		DIN VDE colour code

- Make-up: 			Multi-cores and Multi-pairs

- Screening: 			Overall aluminium foil screen

- Sheath: 			Non-toxic halogen free low smoke flame retardant compound

- Sheath Colour: 		Red as a standard colour (alternative colours on request)

- Required Standard: 		Fire resistance meeting the test requirements of BS EN 50200 for a 30

minute survival time at 840°C, which complies to SANS 10139 standard.

- Voltage: 			300/500V

- Performance: 		PH30 burns for 30 minutes at 840°C

### Fibre Optic Cables

- Low Count Duct Optic Fibre Cable

- The cables shall be specifically designed for employment of low fibre counts in the duct environment.

- These cables shall be suitable for duct applications, both long haul and for LAN backbone in the industrial environment.

- A non-metallic construction shall ensure lightning immunity.

- The cables shall be furnished with high modulus glass strength members, applied contra-helically, to withstand high installation tensions, and to eliminate torsional stresses.

- The tough water resistant outer sheath as well as the gel filled loose tube shall ensure the cables’ suitability for the duct environment.

- The cables shall be available in either flame retardant PVC or Low Smoke Zero Halogen (LSZH), fire retardant, non-toxic sheaths to comply with the strictest building regulations.

- This cable shall be small and lightweight, and tolerate a small bend radius for ease of installation. The small cable size also makes it possible to efficiently utilise duct space.

- Low Loss Single Mode Optic Fibre

- The cables shall be ideally suited for industrial applications, specifically designed for short haul duct installations.

- A non-metallic construction shall ensure lightning immunity.

- These cables shall be robust and provide experimeterent protection from crushing forces.

- They shall provide sustained reliability over a wide temperature range.

- They shall remain relatively stress free while the cable contracts and expands with temperature differences.

- The tough water-resistant sheath and gel filled tubes ensure its suitability for the duct environment.

- In addition, the cable shall be available with a Low Smoke Zero Halogen (LSZH) sheath to comply with the strictest building regulations.

## POWER SUPLIES (Industrial DIN Rail Mounted Power Supplies)

### Primary switched power supply, 1-phase, output current: 5 A

- Input data

- Input nominal voltage range:			220 V AC

- AC frequency:					50 Hz

- Current consumption:				0.9 A (230 V AC)

- Inrush current limitation:				< 15 A

- Power failure bypass:				> 110 ms (230 V AC)

- Typical response time:				< 1 s

- Protective circuitry:					Transient surge protection Varistor

- Input fuse, integrated:				3.15 A (slow-blow, internal)

- Output data

- Nominal output voltage:				24 V DC ±1%

- Setting range of the output voltage:		22.5 V DC to 29.5 V DC

- Output current:					5 A (-25°C to 55°C)

- Current limitation:					Approx. 10 A (for short circuit)

- Max. capacitive load:				Unlimited

- Surge protection against internal surge voltages:	Yes, < 35 V DC

- Degree of protection:				IP20

- Ambient temperature (operation):			-25 °C to 70 °C (> 55° C derating)

- Max. permissible relative humidity (operation):	95 % (at 25°C, no condensation)

### 48 VDC power supplies

- Operating Temperature:				-10 to 60°C

- Relative Humidity:					20 to 90% RH

- Input power:						75 W

- Input nominal voltage range:			220 V AC

- AC frequency:					50 Hz

- Output current:					1.6 A

- Output voltage:					48 V DC

- Output power:					76.8 W

## HIGH SECURITY FENCE SYSTEM

- This shall be a mesh type fence

- It shall be supplied with galvanizing for inland

- There shall be guarantees for the fence

### Double Line Mesh Panel Fence System

The fence system shall comprise of the following components:

- Fence Posts

- Cover Plates

- Top Rails

- Bottom Rails

- Mesh Panels

- Accessories (Bolts, shear off nuts, washers, neoprene strips, etc)

- Top rails

The Top rail shall comply with the following specifications:

- 2.996m x 40 x 40 x 3mm angle iron, predrilled holes for fixing rails to posts & for fixing top section of mesh to rail.

- Top rail to be fitted with 32mm x 2mm serrated comb, fillet welded 10mm at every 100mm centres, including bolts, shear nuts & washers M8 x 30mm stainless steel cup square bolts to fixed rails to posts

- M8 x 40mm stainless steel cup square bolts to fixed top section of mesh to rails

- Coating:

- Hot-dipped galvanised in accordance with ISO 1461

- Minimum Thickness of the Galvanizing: 70μm.

- Bottom rails

The Bottom rail shall comply with the following specifications:

- 2.996m x 40 x 40 x 3mm angle iron, predrilled holes for fixing rails to posts & for fixing top section of mesh to rail, including bolts, shear nuts & washers

- M8 x 30mm stainless steel cup square bolts to fixed rails to posts

- M8 x 40mm stainless steel cup square bolts to fixed bottom section of mesh to rails

- Coating:

- Hot-dipped galvanised in accordance with ISO 1461

- Minimum Thickness of the Galvanizing: 70μm.

- Double Line Mesh Panels

The Double Line Welded Mesh Panels shall comply with the following specifications:

- The mesh panels shall be manufactured from high tensile Galfan Class A coated wire.

- The wire coating should be in accordance with SANS 10244-2:2003 specification (min. 275g/m2).

- Inside apertures: 			76.2mm x 12.7mm

- Wire diameter: 			3.96mm Zincalu

- Width of panel: 			3048mm

- Height of panel: 			2385mm

- Tensile Strength of wire: 		650 – 900 N/mm2

- Weld strength: 			(60 – 80) %

- Coating:

- Hot-dipped galvanised in accordance with ISO 1461

- Minimum Thickness of the Galvanizing: 70μm.

- Cover Plates

- Coating:

- Hot-dipped galvanised in accordance with ISO 1461

- Minimum Thickness of the Galvanizing: 70μm.

- Angle Iron Posts

- 70 x 70 x 6 mm.

- Hot dipped galvanised in accordance with ISO-1461 and pre-drilled with holes for fixing panels, including (70 x 6 mm) cover plate section

- Fixing Accessories

Accessories (Bolts, shear off nuts, washers, neoprene strips, security screws, rivnuts, etc)

- M8 x 40mm Stainless steel countersunk flush lock bolts, stainless steel fender washers

- M8 x 25mm x 2mm & M8 stainless steel shear nuts to attach covering plate and mesh panels to posts.

- M8 x 30mm Stainless steel cup square bolts, stainless steel fender washers M8 x 25mm x 2mm & M8 stainless steel shear nuts to attach bottom & top section of mesh to rails.

- M8 x 50mm Stainless steel cup square bolts, stainless steel fender washers M8 x 25mm x 2mm & M8 stainless steel shear nuts to attach ends of rails to posts

- A self-adhesive 40 mm x 5 mm Neoprene Strip to be placed between the Posts & Panels and between the Panels and the Cover Plates

- Concrete slab for outer security fence

- A 25/19mm concrete slab must be cast in situ along the inside of the external fence.

- The dimensions of the slab shall be as follows: 1300 (Width) x 100mm (Depth) as specified on top of prepared ground level.

- An expansion gap of 50mm wide must be provided at 3000mm intervals, to provide drainage and movement.

- Civil construction will include route preparations, and casting of the 1000mm wide concrete slab on the outside of the fence with welded mesh steel reinforcing to a nominal thickness of 100mm and a minimum compressive strength of 20Mpa.

- The area underneath the concrete plinth shall be cleared of all vegetation prior to casting and treated with a suitable sterilization herbicide to prevent any vegetation growth.

- The contractor shall allow and install a 250micron PVC sheet underneath the concrete slab, to prevent any vegetation growth.

- Sliding Gates

The gate shall be manufactured from mild welded steel tubes, class III hot dip galvanized in and outside to SANS 121:2000 (minimum 275 g/m2, 2 sides combined).

  - 4m Single-leaf Motorized Sliding Gates

| Track System | Motorised Single Leaf |
| --- | --- |
| Gate Width | 4000mm |
| Gate Height (Frame) | 2940mm |
| Colour | Anthracite RAL 7021 |
| Frame | 100mm x 50mm x 2.5mm |
| Vertical Infill frame | 100mm x 50mm x 2.5mm |
| Horizontal Infill frame | 76mm x 50mm x 2.5mm |
| Guide Posts | 100m x 100mm x 6mm |
| End Posts | 100m x 100mm x 6mm |
| Sliding Gate Rack | 30mm x 10mm |
| Sliding Gate track/Ground Rail | 16mm Galvanized Round Bar |
| Sliding Gate Wheels | 100mm Solid Steel “U” Profile Wheel with sealed bearings |
| Sliding Guide Rollers | Nylon Guide Rollers |
| Bearings | 6204 ZZ |

  - 5m Single-leaf Motorized Sliding Gates

| Track System | Motorised Single Leaf |
| --- | --- |
| Gate Width | 5000mm |
| Gate Height (Frame) | 2940mm |
| Colour | Anthracite RAL 7021 |
| Frame | 100mm x 50mm x 2.5mm |
| Vertical Infill frame | 100mm x 50mm x 2.5mm |
| Horizontal Infill frame | 76mm x 50mm x 2.5mm |
| Guide Posts | 100m x 100mm x 6mm |
| End Posts | 100m x 100mm x 6mm |
| Sliding Gate Rack | 30mm x 10mm |
| Sliding Gate track/Ground Rail | 16mm Galvanized Round Bar |
| Sliding Gate Wheels | 100mm Solid Steel “U” Profile Wheel with sealed bearings |
| Sliding Guide Rollers | Nylon Guide Rollers |
| Bearings | 6204 ZZ |

  - Sliding Gate Sweeper

To be installed on the gate in order to sweep the track every time the gate is opened or closed. The sliding gate sweeper shall keep the track or rail clean and free of sand, dust, stones, mud and all other debris that prevent the gate from opening and closing properly.

  - GATE MOTOR

| Input voltage | 220V ± 10% , 50Hz |
| --- | --- |
| Motor voltage | 24V DC |
| Motor power supply | Battery driven (standard capacity – 2 x 7AH) |
| Battery charger | 2A @27.5V |
| Current consumption (mains) | 170mA |
| Current consumption (motor at rated load) | 4A |
| Operator push force – starting | 40kgf |
| Operator push force – rated | 30kgf |
| Gate mass – maximum | 1000kg |
| Gate length – maximum | 100m |
| Gate speed – varies with load | 22 – 26m/min |
| Maximum number of operations per day | 750 |
| Manual override | Lockable lever with key release |
| Operations in standby with 2 x 7AH battery: Half day Full day | 87 69 |
| Collision sensing | Electronic |
| Operating temperature range | -15oC to +50oC |
| Onboard receiver type | Rolling code multi channel |
| Receiver code storage capacity | 500 transmitter buttons |
| Receiver signal frequency | 433MHz |
| Remote gate status indicator |  |

  - INFRA-RED BEAMS

| Power supply | 12V - 24V DC/AC |
| --- | --- |
| Power consumption: Transmitter Receiver | 21mA @ 12V 43mA @ 12V |
| Maximum distance | 40m |
| Contact output rating | 5A@ 220V AC (non conductive) |
| Operating temperature | -15oC to 55oC |
| Operating humidity | 0-90% non condensing |
| IP rating | IP54 |

### Prestressed Hollow-core Fence System

Security wall system

- Prestressed slab

- Depth: 					120mm

- Width: 					1200mm

- Length: 					3000mm

- Min. concrete strength at 28 days: 		50mPa

- Fire rating: 					1 hour

## PERIMETER LIGHTING SYSTEM

### High Performance Security Light Luminaire

# x 26W compact fluorescent

# INGRESS PROTECTION

# Lamp compartment: IP66

# Gear compartment: IP66