## Science Lab Renovation
ITEM NO | ITEM DESCRIPTION | UNIT OF MEASURE | QUANTITY | RATE | AMOUNT
BILL NO. 1
1. | ALTERATIONS (REMOVAL OF EXISTING WORK)
1.1 | Strip all vinyl tiles in the lab area, storeroom, and proposed new office and prepare screeds to receive new vinyl tiles. | Sum | 1 |  | 0
1.2 | Strip all shelving in one of the chemical storerooms in preparation for converting the room into a new office. | Sum | 1 |  | 0
1.3 | Remove all basins and taps on workstations in preparation for installing new ones. | Sum | 1 |  | 0
1.4 | Disconnect all gas points at workstations except for the front row and instructor’s workstations and then plug the hole on workstations countertops with Seligna wood plugs. | Sum | 1 |  | 0
1.5 | Remove the existing and damaged main entrance double door and frame and prepare door opening for a new fire double door and frame. | Sum | 1 |  | 0
1.6 | Remove all existing skirting in preparation to receive new skirting. | Sum | 1 |  | 0
1.7 | Remove all damaged wood panels at desks and prepare the structures for panels replacement. | Sum | 1 |  | 0
1.8 | Take out existing and loose storeroom door in preparation to hang a new one. proofing | Sum | 1 |  | 0
1.9 | Treat the laboratory floor for termites using SABS approved chemicals. the lab, storeroom and teachers room. | Sum | 1 |  | 0
1.10 | Repair ceilings and cornices where required and repaint with two (2) coats of SABS-approved PVA emulsion paint, with colour white. | Sum | 1 |  | 0
| Carried to final summary |  |  |  | 0
BILL NO. 2
2 | THE LAB DESKS RENOVATIONS AND ADDITIONS ( CARPENTRY,JOINERY & ACCESSORIES)
2.1 | Remove, supply, and install new storage credenzas along the science Laboratory walls on either side of the main entrance (double door). Credenza sizes ( H = 840mm, L = 2300mm, B = 630mm), 2 x doors with inner separating shelves, Second Credenza size (H = 840mm, L = 4570mmm, B = 630mm), 5x doors with inner separating shelves. (The total number of credenzas is two(2)) | No | 2 |  | 0
2.2 | Supply and fit Masonite wood finish storeroom door, including door lock and handle with Dorma “CB30” satin chrome lever and hinges (2X) suitable for a single door | Sum | 1 |  | 0
2.3 | A 5–10 mm shadow line is allowed for between the modesty panel and top. Desks tops will be fixed to epoxy powder-coated steel frames and fixed to the concrete surface. | No | 21 |  | 0
2.4 | Replace all lab chairs with stools appriopriate for lab functions and lab desks height | No | 32 |  | 0
2.5 | Remove carefully the wooden Table Tops (workstations), Sand down all workstation tops, and revarnish with 2 coats of clear varnish. Paint to be SABS-approved | No | 7 |  | 0
2.6 | Make two (2) additional basin holes on either side of the workstations (Learners only), dimensions of the new additional basin holes ( L = 41mm, B = 31mm) Note: The height of all Table Tops ( Workstations) is 940mm. Note: There will be 2 cut-outs per 6 x Workstation Table (18 x cut-outs in total) | No | 12 |  | 0
2.7 | Remove carefully all Steel Frames and repaint with two coats of enamel suitable for steel surfaces. There are 6 x Learners Tables and 1 x Educators Table. Paint to be SABS-approved enamel one. | No | 7 |  | 0
2.8 | Re-instate all the newly cut-out Workstations | No | 6 |  | 0
2.9 | Re-instate all the re-painted steel support frames for mounting the Workstation Table Tops. (6x Learners and 1x Educators) | No | 7 |  | 0
2.10 | Supply science Laboratory stools for Learners and an Educator (refer to the picture on the RFQ document for the type of stools) | No | 19 |  | 0
2.11 | Build-in double steel frame and hang a fire double door, including door lock with Dorma “CB30” satin chrome lever and hinges suitable for a double door at Lab main entrance. (Double door dimensions L = 1540mm, H = 2040mm) | No | 1 |  | 0
2.12 | Paint main entrance fire doors with two (2) coats of SABS-approved paint. The paint colour to be the same as the other two inside New-Office and Chemical Storage Doors. | No | 2 |  | 0
2.13 | Remove and re-instate the burglar doors outside the Main Entrance Double Door of the Science Laboratory | No | 2 |  | 0
2.14 | Build the Main Entrance Door Ramp on the outside to allow easy access into the Science Laboratory for disabled persons. ( L = 1600mm across the double door, with 10mm sloping on either side of the door opening, height of the ramp = 150mm, and 80mm long from the Main double door entry to the end of the ramp in front of the main double door entrance) | sum | 1 |  | 0
2.15 | Clean shelving in existing storeroom, make good and repaint wood shelves with two (2) coats of clear varnish. Paint to be SABS approved. | sum | 1 |  | 0
2.16 | Clean the existing Cabinet Display Unit at the back of the Science Laboratory, make good, and repaint wood shelves with two (2) coats of clear varnish. Paint to be SABS approved. | sum | 1 |  | 0
2.17 | Procure office Table for the new office (An office chair exists). The size of the table, L = 1500mm, B = 610mm and H = 750mm | No | 1 |  | 0
| Carried to final summary |  |  |  | 0
BILL NO. 3
3. | FLOORING
3.1 | Supply and install FloorworX Superflex (or Similar approved) fully flexible vinyl floor tiles 610 mm x 610 mm x 2,0mm thick, manufactured in accordance with SANS 786:2000, laid in FloorworX No. 62 Plus acrylic adhesive (or similar approved) spread with a notched trowel on suitably prepared subfloor (elsewhere specified) with a hygrometer reading showing a moisture content of less than 70% and rolled with 68 kg three section metal roller on completion. | m2 | 139 |  | 0
3.2 | Fit meranti skirting after laying of vinyl tiles | m | 74 |  | 0
| Carried to final summary |  |  |  | 0
BILL NO. 4
4. | PLUMBING INSTALLATION
4.1 | Remove all existing basins (x7) and install new basins ( x12). The New basins will be installed on the refurbished Table/Countertops ( Learners and Educator). Note: There are 6 x existing basins ( Learners) and 1 on the Educator's countertops ( Total existing 7 basins, New basins will be 18 + 1 (19) | No | 19 |  | 0
4.2 | Install new cold water tap appriopriate for lab use | No | 19 |  | 0
4.3 | Supply and install water reticulation to lab desk basins | Lot | 1 |  | 0
4.4 | Install new drainage pipes for lab desk basins | Lot | 1 |  | 0
4.5 | Cut out openings in workstations Table/Countertops to increase sinks and taps to a capacity of three (3) per workstation | No | 12 |  | 0
4.6 | Water reticulation to allow for safe disposal of chemicals. A pit must be constructed for this purpose. Supply and install Chemical Conservancy Tank (1500L Tank, Diameter 1550mm, H = 1280mm, Lid =250mm). Refer to the RFQ documentation for more details | No | 1 |  | 0
4.7 | The tank should be secured underground, away from access to learners but should allow for easy access for safe disposal of contents once full. | Lot | 1 |  | 0
4.8 | The Bidder must ensure that the tank is a Conservancy Tank that is chemical resistant instead of a septic tank. It must be installed as per the manufacturer’s instruction | sum | 1 |  | 0
4.9 | Trace the output pipe from the nearest point to the science lab, where the main line connection can be made. | sum | 1 |  | 0
4.10 | Only a certified plumber who knows plumbing installation for the school’s science laboratory must be appointed by the successful bidder. A plumbing Certificate of Compliance (COC) must be issued on completion of the work | sum | 1 |  | 0
| Carried to final summary |  |  |  | 0
BILL NO. 5
5. | PAINTWORKS
5.1 | Science lab (9,1m x 3m) x 2 sides, and (12m x 3m) x 2sides less Windows x10 | m2 | 112 |  | 0
5.2 | Ceiling in science lab to be white for (12m x 9m) | m2 | 108 |  | 0
5.3 | New Teachers's room wall paintings (3.85m x 3m) x 2 sides and (3m x 3m) x2 sides | m2 | 41.1 |  | 0
5.4 | Chemical storeroom to be painted for ceiling (5mx3m) | m2 | 15 |  | 0
5.5 | Chemical storeroom to be painted for Walls (3mx3m) x 4 sides | m2 | 25.5 |  | 0
| Carried to final summary |  |  |  | 0
BILL NO. 6
6. | ELECTRICAL & MECHANICAL INSTALLATION
6.1 | Replace old fluorescent light fittings (1,5m long) with new fittings and LED light tubes. | No | 6 |  | 0
6.2 | Replace old bulkhead lights with new fittings and LED light tubes. (Old Chemical Room and Storage Room) | No | 2 |  | 0
6.3 | Disconnect old double plugs mounted on the side of the existing table tops (children) | No |  |  | 0
6.4 | supply and install new Electrical double plugs on both sides of each table top ( 6 x 2) | No | 12 |  | 0
6.5 | supply and install new Electrical double plug on one side of the Teachers Table Top | No | 1 |  | 0
6.6 | Repair general electrical installations where required, including the Distribution Board and power points | Sum | 1 |  | 0
6.7 | Allow provisional sum for rectifying of electrical works | Sum | 1 |  | 0
6.8 | Supply and install Air Conditioner System (Inverter) Split Unit rated 24 000 BTU. This will be a wall-mounted unit with the condenser to be placed outside. | No | 1 |  | 0
6.9 | Issue Electrical Certificate of Compliance (COC) for completed works. (Only a Certified Electrician must be appointed by the successful Bidder)
6.10 | Provision sum for Electrical works | sum | 1 |  | 50000
| Carried to final summary |  |  |  | 50000
BILL NO. 7
7 | FIRE INSTALLATIONS AND GAS RETICULATION
7.1 | Repair, install fire hose and make good fire reel situated outside the Science laboratory | Sum | 1 |  | 0
7.2 | Install a new fire extinguisher cabinet and 7.5kg fire extinguisher outside the lab to replace the damaged one. | Sum | 1 |  | 0
7.3 | Instal 7.5kg fire extinguisher in the chemical storeroom to replace the missing one. | Sum | 1 |  | 0
7.4 | Supply and fit 2 x 48kg gas cylinders in a fitted steel cage (outside the Science Laboratory), including reticulation to gas points at all workstations including the Teacher's front Table. | Sum | 1 |  | 0
7.5 | Provide gas burners to all workstations as per Department of Basic Education specification. The number of gas points (6 x2) and burners (6 x2). Total number of gas points is 12 and the burners are 12 as well. | No | 1 |  | 0
7.6 | Issue Gas Certificate of Compliance (COC) for completed works. (Only a Certified Gas installer must be appointed by the successful Bidder) | Sum | 1 |  | 0
7.7 | Allow provisional sum for gas reticulation | Sum | 1 |  | 0
| Carried to final summary |  |  |  | 0
BILL NO. 8
8. | FUME CABINET
8.1 | Supply and installation, by a specialist contractor, a ViVid Air VA600S or similar approved School Fume Extraction Cabinet with a size of 2120 mm high by 1000 mm wide with ancillary material and installation labor. See attached picture on the RFQ document | Sum | 1 |  | 0
8.2 | Electrical Power supply (15A) double socket to be supplied and installed on the table (floor area) to connect the Fume Cabinet | No | 1 |  | 0
| Carried to final summary |  |  |  | 0
BILL NO. 9
9. | GENERAL ITEMS
9.1 | Supply and install ceiling mounted video projector for projections on the WTB | No | 1 |  | 0
9.3 | Supply and install window blinds for the existing windows to cover 10 windows of the dimensions One set of Blinds (L = 1470mm, H = 1500mm) x 6 and another set of Blinds dimension (L = 1940mm, H = 600mm) x 4. Note: The Blinds must be durable and of the same quality as the existing ones | No | 10 |  | 0
9.5 | Supply and install new whiteboard as replacement for existing one (white board measurements: 1.2m x3m | No | 1 |  | 0
9.6 | Supply and install projector roll-down screen (Dimensions 1.2m x3m) | No | 1 |  | 0
9.7 | Pest control in and around the existing lab | Sum | 1 |  | 0
| Carried to final summary |  |  |  | 0

## Final summary
Item No. | Description | Unit | Quantity | Amount
BILL NO. 1 | ALTERATIONS (REMOVAL OF EXISTING WORK) | Item | Sum | 0
BILL NO. 2 | THE LAB DESKS RENOVATIONS AND ADDITIONS ( CARPENTRY,JOINERY & ACCESSORIES) | Item | Sum | 0
BILL NO. 3 | FLOORING | Item | Sum | 0
BILL NO. 4 | PLUMBING INSTALLATION | Item | Sum | 0
BILL NO. 5 | PAINTWORKS | Item | Sum | 0
BILL NO. 6 | ELECTRICAL & MECHANICAL INSTALLATION | Item | Sum | 50000
BILL NO. 7 | FIRE INSTALLATIONS AND GAS RETICULATION | Item | Sum | 0
BILL NO. 9 | FUME CABINET | Item | Sum | 0
BILL NO. 10 | GENERAL ITEMS | Item | Sum | 0
| Total |  |  | 50000